## NMU Summary
Summary of inverter data - NMU South Campus (March - August 2020)
| Solar Yield | [6 empty] | Plant section | Azimuth | Inclination | Inverter | Qty | kWac
NMU Plant | February | March | April | May | June | July | August | East wing | 10° | 30° | Platinum 7200TLD | 9 | 62.1
East wing | 9262.747 | 9991.392 | 9206.387 | 8095.672 | 7411.494 | 8373.501 | 8690.206 | PL22k | 0° | 30° | Platinum 22000TLD | 3 | 62.1
PL22k | 8119.284 | 8779.944 | 8183.861 | 7378.964 | 6946.913 | 8370.931 | 8900.189 | Pl72C | 0° | 30° | Platinum 7200TLD | 12 | 82.8
Pl72C | 12031.284 | 12985.259 | 12046.134 | 10660.338 | 9787.909 | 11031.308 | 11575.495 | PL-R3 | 0° | 30° | Platinum R3-16k | 10 | 150
PL-R3 | 22292.546 | 22786.65 | 20848.252 | 18059.918 | 15601.191 | 17590.995 | 20099.464 | STP60 | 0° | 30° | SMA STP60-10 | 4 | 240
STP60 | 33441.4 | 36693.6 | 35858.4 | 31416.87 | 28725.05 | 31500.6 | 33800.2 | STP20-F | 0° | 30° | SMA STP20 | 2 | 40
STP20-F | 5608.961 | 6065.889 | 5651.184 | 5056.725 | 4493.852 | 5057.436 | 5592.51 | West wing | -10° | 30° | Platinum 7200TLD | 9 | 62.1
West wing | 9092.078 | 9465.558 | 8367.331 | 5805.671 | 6490.086 | 7309.478 | 7847.984 | Tracker-1 | Tracked | Tracked | SMA STP20 | 7 | 140
Tracker-1 | 25589.652 | 11886.184 | 375.222 | 20483.026 | 21561.675 | 23996.896 | 24869.89 | Tracker-2 | Tracked | Tracked | SMA STP20 | 8 | 160
Tracker-2 | 28066.518 | 29276.394 | 25676.785 | 21152.85 | 20776.207 | 25504.812 | 26454.714 | [5 empty] | 999.1
Plant total | 153504.47 | 147930.87 | 126213.556 | 128110.034 | 121794.377 | 138735.957 | 147830.652
Projected | 173140 | 172670 | 154540 | 146900 | 133980 | 145130 | 159030
Janitza | 164993,8* | 138203.9 | 106713.2 | 102336.6 | 103720 | 120400 | 114252.5
Difference | -11489.33 | 9726.97 | 19500.356 | 25773.434 | 18074.377 | 18335.957 | 33578.152
Variance | 107.5% | 93.42% | 84.55% | 79.88% | 85.16% | 86.78% | 77.29%
Total (period) | 964119.916
Projected (period) | 1085390
Variance | 88.83%
*Substation A meter reading for Febraury includes 30 & 31 January = 11490kWh
Notable yield losses
11 - 13 March 2020 | A fault at the NMU Substation A breaker led to two days of lost production spread over three days
17 March - 30 April | An electrical fault at the main junction box for Tracker section 1 led to production losses. As a
result of the COVID-19 lockdown, this fault was only repaired on 30 April 2020.
Load shedding | Rolling power outages since February 2020 have led to continuing yield losses of varying proportions
depending on the time of day that NMU is subject to power outages.
Metering discrepancy | The Janitza utility meter installed at the PV plant minisub has been compromised since March 2020.
Four SMA STP60 inverters are not currently monitored on the Solar Log as a result of a faulty
Inverter Manager from SMA. The information in this document is a combination of Solar Log data
and physical readings taken manually from the STP60 inverters.
To correct this discrepancy, new metering CT's are being installed on Friday, 4 September. The meter
accuracy will be tested on the same day and where necessary, the software settings will be adjusted.
Inverters repaired | In July repairs were carried out to replace one Platinum 7200TLD inverter on the West Wing and to
repair one Platinum 22000TLD inverter which was only operating at 66% capacity.
We have also repaired 2 faulty Platinum 7200TLD inverters both of which are now on site as spares.
Tracker maintenance | In June & July, full maintenance and repairs were carried out on all trackers.
Notes | The "Target" column is an internally calculated daily average of the Solar Log based on Geographic
data and month of the year

## Feb 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
February | Yield | Target | Variance |  | February | Yield | Target | Variance |  | February | Yield | Target | Variance |  | February | Yield | Target | Variance
1 | 271449 | 318446 | -14.76% |  | 1 | 240825 | 363227 | -33.7% |  | 1 | 355937 | 477669 | -25.48% |  | 1 | 268857 | 358251 | -24.95%
2 | 231573 | 318446 | -27.28% |  | 2 | 204789 | 363227 | -43.62% |  | 2 | 302333 | 477669 | -36.71% |  | 2 | 230625 | 358251 | -35.62%
3 | 345471 | 318446 | 8.487% |  | 3 | 302140 | 363227 | -16.82% |  | 3 | 450025 | 477669 | -5.787% |  | 3 | 340744 | 358251 | -4.887%
4 | 363073 | 318446 | 14.01% |  | 4 | 318360 | 363227 | -12.35% |  | 4 | 471611 | 477669 | -1.268% |  | 4 | 356087 | 358251 | -0.604%
5 | 311880 | 318446 | -2.062% |  | 5 | 271484 | 363227 | -25.26% |  | 5 | 399244 | 477669 | -16.42% |  | 5 | 302973 | 358251 | -15.43%
6 | 42005 | 318446 | -86.81% |  | 6 | 37390 | 363227 | -89.71% |  | 6 | 55053 | 477669 | -88.47% |  | 6 | 41288 | 358251 | -88.48%
7 | 93318 | 318446 | -70.7% |  | 7 | 83702 | 363227 | -76.96% |  | 7 | 123544 | 477669 | -74.14% |  | 7 | 92815 | 358251 | -74.09%
8 | 266570 | 318446 | -16.29% |  | 8 | 234836 | 363227 | -35.35% |  | 8 | 349932 | 477669 | -26.74% |  | 8 | 262428 | 358251 | -26.75%
9 | 279336 | 318446 | -12.28% |  | 9 | 247637 | 363227 | -31.82% |  | 9 | 367082 | 477669 | -23.15% |  | 9 | 277186 | 358251 | -22.63%
10 | 244984 | 318446 | -23.07% |  | 10 | 213870 | 363227 | -41.12% |  | 10 | 315886 | 477669 | -33.87% |  | 10 | 239825 | 358251 | -33.06%
11 | 453489 | 318446 | 42.41% |  | 11 | 395524 | 363227 | 8.892% |  | 11 | 588584 | 477669 | 23.22% |  | 11 | 444285 | 358251 | 24.02%
12 | 457890 | 318446 | 43.79% |  | 12 | 399014 | 363227 | 9.853% |  | 12 | 593708 | 477669 | 24.29% |  | 12 | 448243 | 358251 | 25.12%
13 | 391039 | 318446 | 22.8% |  | 13 | 339192 | 363227 | -6.617% |  | 13 | 503847 | 477669 | 5.48% |  | 13 | 383372 | 358251 | 7.012%
14 | 443656 | 318446 | 39.32% |  | 14 | 386538 | 363227 | 6.418% |  | 14 | 575067 | 477669 | 20.39% |  | 14 | 433611 | 358251 | 21.04%
15 | 156750 | 318446 | -50.78% |  | 15 | 141062 | 363227 | -61.16% |  | 15 | 209114 | 477669 | -56.22% |  | 15 | 157590 | 358251 | -56.01%
16 | 191746 | 318446 | -39.79% |  | 16 | 171248 | 363227 | -52.85% |  | 16 | 253799 | 477669 | -46.87% |  | 16 | 191566 | 358251 | -46.53%
17 | 327441 | 318446 | 2.825% |  | 17 | 286367 | 363227 | -21.16% |  | 17 | 417407 | 477669 | -12.62% |  | 17 | 318036 | 358251 | -11.23%
18 | 172527 | 318446 | -45.82% |  | 18 | 152782 | 363227 | -57.94% |  | 18 | 223917 | 477669 | -53.12% |  | 18 | 169138 | 358251 | -52.79%
19 | 443978 | 318446 | 39.42% |  | 19 | 387170 | 363227 | 6.592% |  | 19 | 576259 | 477669 | 20.64% |  | 19 | 435294 | 358251 | 21.51%
20 | 397213 | 318446 | 24.73% |  | 20 | 349947 | 363227 | -3.656% |  | 20 | 521509 | 477669 | 9.178% |  | 20 | 392428 | 358251 | 9.54%
21 | 316444 | 318446 | -0.6287% |  | 21 | 277884 | 363227 | -23.5% |  | 21 | 413855 | 477669 | -13.36% |  | 21 | 312485 | 358251 | -12.77%
22 | 336203 | 318446 | 5.576% |  | 22 | 294536 | 363227 | -18.91% |  | 22 | 437219 | 477669 | -8.468% |  | 22 | 328591 | 358251 | -8.279%
23 | 424051 | 318446 | 33.16% |  | 23 | 369776 | 363227 | 1.803% |  | 23 | 547813 | 477669 | 14.68% |  | 23 | 413950 | 358251 | 15.55%
24 | 446060 | 318446 | 40.07% |  | 24 | 388770 | 363227 | 7.032% |  | 24 | 578730 | 477669 | 21.16% |  | 24 | 436811 | 358251 | 21.93%
25 | 451631 | 318446 | 41.82% |  | 25 | 392744 | 363227 | 8.126% |  | 25 | 584575 | 477669 | 22.38% |  | 25 | 441794 | 358251 | 23.32%
26 | 368146 | 318446 | 15.61% |  | 26 | 324523 | 363227 | -10.66% |  | 26 | 475361 | 477669 | -0.4832% |  | 26 | 360453 | 358251 | 0.6147%
27 | 338069 | 318446 | 6.162% |  | 27 | 295520 | 363227 | -18.64% |  | 27 | 435776 | 477669 | -8.77% |  | 27 | 329180 | 358251 | -8.115%
28 | 247111 | 318446 | -22.4% |  | 28 | 219267 | 363227 | -39.63% |  | 28 | 320313 | 477669 | -32.94% |  | 28 | 241998 | 358251 | -32.45%
29 | 449644 | 318446 | 41.2% |  | 29 | 392387 | 363227 | 8.028% |  | 29 | 583784 | 477669 | 22.22% |  | 29 | 440425 | 358251 | 22.94%
| 9262.747 |  |  |  |  | 8119.284 |  |  |  |  | 12031.284 |  |  |  |  | 9092.078
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
February | Yield | Target | Variance |  | February | Yield | Target | Variance |  | February | Yield | Target | Variance |  | February | Yield | Target | Variance
1 | 615578 | 884571 | -30.41% |  | 1 | 151313 | 221143 | -31.58% |  | 1 | 726864 | 973800 | -25.36% |  | 1 | 774106 | 1112914 | -30.44%
2 | 1034236 | 884571 | 16.92% |  | 2 | 136622 | 221143 | -38.22% |  | 2 | 551767 | 973800 | -43.34% |  | 2 | 626785 | 1112914 | -43.68%
3 | 791843 | 884571 | -10.48% |  | 3 | 193875 | 221143 | -12.33% |  | 3 | 991690 | 973800 | 1.837% |  | 3 | 1051526 | 1112914 | -5.516%
4 | 816375 | 884571 | -7.709% |  | 4 | 222342 | 221143 | 0.5422% |  | 4 | 966858 | 973800 | -0.7129% |  | 4 | 1089686 | 1112914 | -2.087%
5 | 688223 | 884571 | -22.2% |  | 5 | 201594 | 221143 | -8.84% |  | 5 | 850029 | 973800 | -12.71% |  | 5 | 957003 | 1112914 | -14.01%
6 | 86858 | 884571 | -90.18% |  | 6 | 26209 | 221143 | -88.15% |  | 6 | 86593 | 973800 | -91.11% |  | 6 | 107942 | 1112914 | -90.3%
7 | 198842 | 884571 | -77.52% |  | 7 | 45200 | 221143 | -79.56% |  | 7 | 174789 | 973800 | -82.05% |  | 7 | 202781 | 1112914 | -81.78%
8 | 596731 | 884571 | -32.54% |  | 8 | 139391 | 221143 | -36.97% |  | 8 | 656011 | 973800 | -32.63% |  | 8 | 725560 | 1112914 | -34.81%
9 | 575573 | 884571 | -34.93% |  | 9 | 151166 | 221143 | -31.64% |  | 9 | 774361 | 973800 | -20.48% |  | 9 | 824048 | 1112914 | -25.96%
10 | 728627 | 884571 | -17.63% |  | 10 | 152725 | 221143 | -30.94% |  | 10 | 710784 | 973800 | -27.01% |  | 10 | 770568 | 1112914 | -30.76%
11 | 1038172 | 884571 | 17.36% |  | 11 | 280586 | 221143 | 26.88% |  | 11 | 1364400 | 973800 | 40.11% |  | 11 | 1482789 | 1112914 | 33.23%
12 | 1027384 | 884571 | 16.14% |  | 12 | 282339 | 221143 | 27.67% |  | 12 | 1385333 | 973800 | 42.26% |  | 12 | 1493177 | 1112914 | 34.17%
13 | 847146 | 884571 | -4.231% |  | 13 | 263418 | 221143 | 19.12% |  | 13 | 1149207 | 973800 | 18.01% |  | 13 | 1268888 | 1112914 | 14.01%
14 | 999352 | 884571 | 12.98% |  | 14 | 275888 | 221143 | 24.76% |  | 14 | 1336696 | 973800 | 37.27% |  | 14 | 1438019 | 1112914 | 29.21%
15 | 357349 | 884571 | -59.6% |  | 15 | 64102 | 221143 | -71.01% |  | 15 | 327322 | 973800 | -66.39% |  | 15 | 354866 | 1112914 | -68.11%
16 | 740306 | 884571 | -16.31% |  | 16 | 107171 | 221143 | -51.54% |  | 16 | 503423 | 973800 | -48.3% |  | 16 | 553350 | 1112914 | -50.28%
17 | 745985 | 884571 | -15.67% |  | 17 | 208088 | 221143 | -5.903% |  | 17 | 787535 | 973800 | -19.13% |  | 17 | 896136 | 1112914 | -19.48%
18 | 387467 | 884571 | -56.2% |  | 18 | 107883 | 221143 | -51.22% |  | 18 | 441285 | 973800 | -54.68% |  | 18 | 503373 | 1112914 | -54.77%
19 | 1001485 | 884571 | 13.22% |  | 19 | 278811 | 221143 | 26.08% |  | 19 | 1309430 | 973800 | 34.47% |  | 19 | 1432406 | 1112914 | 28.71%
20 | 910345 | 884571 | 2.914% |  | 20 | 222388 | 221143 | 0.563% |  | 20 | 972758 | 973800 | -0.107% |  | 20 | 1074819 | 1112914 | -3.423%
21 | 716123 | 884571 | -19.04% |  | 21 | 201049 | 221143 | -9.086% |  | 21 | 861976 | 973800 | -11.48% |  | 21 | 961148 | 1112914 | -13.64%
22 | 1313199 | 884571 | 48.46% |  | 22 | 202032 | 221143 | -8.642% |  | 22 | 933700 | 973800 | -4.118% |  | 22 | 1026285 | 1112914 | -7.784%
23 | 940162 | 884571 | 6.285% |  | 23 | 267168 | 221143 | 20.81% |  | 23 | 1209685 | 973800 | 24.22% |  | 23 | 1322885 | 1112914 | 18.87%
24 | 961175 | 884571 | 8.66% |  | 24 | 281026 | 221143 | 27.08% |  | 24 | 1332376 | 973800 | 36.82% |  | 24 | 1432984 | 1112914 | 28.76%
25 | 1018688 | 884571 | 15.16% |  | 25 | 271565 | 221143 | 22.8% |  | 25 | 1283508 | 973800 | 31.8% |  | 25 | 1401464 | 1112914 | 25.93%
26 | 824591 | 884571 | -6.781% |  | 26 | 233262 | 221143 | 5.48% |  | 26 | 1094961 | 973800 | 12.44% |  | 26 | 1191451 | 1112914 | 7.057%
27 | 761375 | 884571 | -13.93% |  | 27 | 218378 | 221143 | -1.25% |  | 27 | 866189 | 973800 | -11.05% |  | 27 | 977802 | 1112914 | -12.14%
28 | 552413 | 884571 | -37.55% |  | 28 | 153764 | 221143 | -30.47% |  | 28 | 672833 | 973800 | -30.91% |  | 28 | 750385 | 1112914 | -32.57%
29 | 1016943 | 884571 | 14.96% |  | 29 | 269606 | 221143 | 21.91% |  | 29 | 1267289 | 973800 | 30.14% |  | 29 | 1374286 | 1112914 | 23.49%
| 22292.546 |  |  |  |  | 5608.961 |  |  |  |  | 25589.652 |  |  |  |  | 28066.518
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 9262.747
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 8119.284
| 2020-01-31 |  |  |  |  | 2020-01-31 |  | 62375 |  |  | 2020-01-31 |  | 58073.6 |  |  | Pl72C | 12031.284
| 2020-02-03 | 3 |  | 3277.6 |  | 2020-02-03 | 3 | 63190.7 | 815.7 |  | 2020-02-03 | 3 | 58896.7 | 823.1 |  | PL-R3 | 22292.546
| 2020-02-04 | 1 |  | 1462.2 |  | 2020-02-04 | 1 | 63556.5 | 365.8 |  | 2020-02-04 | 1 | 59262 | 365.3 |  | STP60 | 33441.4
| 2020-02-05 | 1 |  | 1249 |  | 2020-02-05 | 1 | 63868.4 | 311.9 |  | 2020-02-05 | 1 | 59574.6 | 312.6 |  | STP20-F | 5608.961
| 2020-02-06 | 1 |  | 167.6 |  | 2020-02-06 | 1 | 63910.8 | 42.4 |  | 2020-02-06 | 1 | 59616 | 41.4 |  | West wing | 9092.078
| 2020-02-07 | 1 |  | 346.2 |  | 2020-02-07 | 1 | 63997 | 86.2 |  | 2020-02-07 | 1 | 59702.9 | 86.9 |  | Tracker-1 | 25589.652
| 2020-02-10 | 3 |  | 2889.8 |  | 2020-02-10 | 3 | 64716.7 | 719.7 |  | 2020-02-10 | 3 | 60428.1 | 725.2 |  | Tracker-2 | 28066.518
| 2020-02-11 | 1 |  | 1644.8 |  | 2020-02-11 | 1 | 65126.5 | 409.8 |  | 2020-02-11 | 1 | 60840.7 | 412.6
| 2020-02-12 | 1 |  | 1718.4 |  | 2020-02-12 | 1 | 65554.8 | 428.3 |  | 2020-02-12 | 1 | 61271.6 | 430.9 |  | Plant total | 153504.47
| 2020-02-14 | 2 |  | 1878 |  | 2020-02-14 | 2 | 66026.6 | 471.8 |  | 2020-02-14 | 2 | 61738.8 | 467.2 |  | Janitza | 164993.8
| 2020-02-15 | 1 |  | 1272.8 |  | 2020-02-15 | 1 | 66343.9 | 317.3 |  | 2020-02-15 | 1 | 62057.9 | 319.1 |  | Difference | -11489.33
| 2020-02-17 | 2 |  | 2810.8 |  | 2020-02-17 | 2 | 67045.2 | 701.3 |  | 2020-02-17 | 2 | 62762 | 704.1 |  |  | 107.5%
| 2020-02-18 | 1 |  | 610.2 |  | 2020-02-18 | 1 | 67197.1 | 151.9 |  | 2020-02-18 | 1 | 62915.2 | 153.2
| 2020-02-19 | 1 |  | 1578.2 |  | 2020-02-19 | 1 | 67590.5 | 393.4 |  | 2020-02-19 | 1 | 63310.9 | 395.7
| 2020-02-20 | 1 |  | 1634.8 |  | 2020-02-20 | 1 | 67998.6 | 408.1 |  | 2020-02-20 | 1 | 63720.2 | 409.3
| 2020-02-21 | 1 |  | 1210.6 |  | 2020-02-21 | 1 | 68299.8 | 301.2 |  | 2020-02-21 | 1 | 64024.3 | 304.1
| 2020-02-24 | 3 |  | 4347.6 |  | 2020-02-24 | 3 | 69383.5 | 1083.7 |  | 2020-02-24 | 3 | 65114.4 | 1090.1
| 2020-02-25 | 1 |  | 1698.8 |  | 2020-02-25 | 1 | 69806.8 | 423.3 |  | 2020-02-25 | 1 | 65540.5 | 426.1
| 2020-02-26 | 1 |  | 1397.8 |  | 2020-02-26 | 1 | 70155.7 | 348.9 |  | 2020-02-26 | 1 | 65890.5 | 350
| 2020-02-27 | 1 |  | 1427.4 |  | 2020-02-27 | 1 | 70511.7 | 356 |  | 2020-02-27 | 1 | 66248.2 | 357.7
| 2020-02-28 | 1 |  | 818.8 |  | 2020-02-28 | 1 | 70715.8 | 204.1 |  | 2020-02-28 | 1 | 66453.5 | 205.3
|  | 28 |  | 33441.4 |  |  | 28 |  | 8340.8 |  |  | 28 |  | 8379.9

## Mar 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
March | Yield | Target | Variance |  | March | Yield | Target | Variance |  | March | Yield | Target | Variance |  | March | Yield | Target | Variance
1 | 433751 | 287628 | 50.8% |  | 1 | 378644 | 328076 | 15.41% |  | 1 | 562028 | 431443 | 30.27% |  | 1 | 424141 | 323582 | 31.08%
2 | 408585 | 287628 | 42.05% |  | 2 | 356877 | 328076 | 8.779% |  | 2 | 527135 | 431443 | 22.18% |  | 2 | 396827 | 323582 | 22.64%
3 | 394761 | 287628 | 37.25% |  | 3 | 346503 | 328076 | 5.617% |  | 3 | 513983 | 431443 | 19.13% |  | 3 | 385494 | 323582 | 19.13%
4 | 289351 | 287628 | 0.599% |  | 4 | 252869 | 328076 | -22.92% |  | 4 | 374286 | 431443 | -13.25% |  | 4 | 283635 | 323582 | -12.35%
5 | 405774 | 287628 | 41.08% |  | 5 | 356612 | 328076 | 8.698% |  | 5 | 526195 | 431443 | 21.96% |  | 5 | 395770 | 323582 | 22.31%
6 | 389411 | 287628 | 35.39% |  | 6 | 339584 | 328076 | 3.508% |  | 6 | 502536 | 431443 | 16.48% |  | 6 | 378274 | 323582 | 16.9%
7 | 410422 | 287628 | 42.69% |  | 7 | 359138 | 328076 | 9.468% |  | 7 | 532310 | 431443 | 23.38% |  | 7 | 401968 | 323582 | 24.22%
8 | 341065 | 287628 | 18.58% |  | 8 | 300338 | 328076 | -8.455% |  | 8 | 443947 | 431443 | 2.898% |  | 8 | 335024 | 323582 | 3.536%
9 | 80067 | 287628 | -72.16% |  | 9 | 71267 | 328076 | -78.28% |  | 9 | 104280 | 431443 | -75.83% |  | 9 | 78636 | 323582 | -75.7%
10 | 165322 | 287628 | -42.52% |  | 10 | 149068 | 328076 | -54.56% |  | 10 | 216213 | 431443 | -49.89% |  | 10 | 164021 | 323582 | -49.31%
11 | 100198 | 287628 | -65.16% |  | 11 | 90078 | 328076 | -72.54% |  | 11 | 131831 | 431443 | -69.44% |  | 11 | 99587 | 323582 | -69.22%
12 | 0 | 287628 | -100% |  | 12 | 0 | 328076 | -100% |  | 12 | 0 | 431443 | -100% |  | 12 | 0 | 323582 | -100%
13 | 96458 | 287628 | -66.46% |  | 13 | 89892 | 328076 | -72.6% |  | 13 | 134257 | 431443 | -68.88% |  | 13 | 95617 | 323582 | -70.45%
14 | 368502 | 287628 | 28.12% |  | 14 | 320636 | 328076 | -2.268% |  | 14 | 465531 | 431443 | 7.901% |  | 14 | 355018 | 323582 | 9.715%
15 | 119281 | 287628 | -58.53% |  | 15 | 105844 | 328076 | -67.74% |  | 15 | 155354 | 431443 | -63.99% |  | 15 | 117199 | 323582 | -63.78%
16 | 405959 | 287628 | 41.14% |  | 16 | 356413 | 328076 | 8.637% |  | 16 | 526968 | 431443 | 22.14% |  | 16 | 397118 | 323582 | 22.73%
17 | 348557 | 287628 | 21.18% |  | 17 | 306367 | 328076 | -6.617% |  | 17 | 452573 | 431443 | 4.898% |  | 17 | 341604 | 323582 | 5.57%
18 | 424565 | 287628 | 47.61% |  | 18 | 373504 | 328076 | 13.85% |  | 18 | 553447 | 431443 | 28.28% |  | 18 | 414715 | 323582 | 28.16%
19 | 412937 | 287628 | 43.57% |  | 19 | 361480 | 328076 | 10.18% |  | 19 | 536531 | 431443 | 24.36% |  | 19 | 403681 | 323582 | 24.75%
20 | 395614 | 287628 | 37.54% |  | 20 | 347761 | 328076 | 6% |  | 20 | 513778 | 431443 | 19.08% |  | 20 | 386019 | 323582 | 19.3%
21 | 417289 | 287628 | 45.08% |  | 21 | 366128 | 328076 | 11.6% |  | 21 | 542017 | 431443 | 25.63% |  | 21 | 406594 | 323582 | 25.65%
22 | 366300 | 287628 | 27.35% |  | 22 | 320645 | 328076 | -2.265% |  | 22 | 475920 | 431443 | 10.31% |  | 22 | 357967 | 323582 | 10.63%
23 | 291260 | 287628 | 1.263% |  | 23 | 256691 | 328076 | -21.76% |  | 23 | 376191 | 431443 | -12.81% |  | 23 | 249789 | 323582 | -22.81%
24 | 219652 | 287628 | -23.63% |  | 24 | 193665 | 328076 | -40.97% |  | 24 | 284017 | 431443 | -34.17% |  | 24 | 188750 | 323582 | -41.67%
25 | 385264 | 287628 | 33.95% |  | 25 | 338854 | 328076 | 3.285% |  | 25 | 504370 | 431443 | 16.9% |  | 25 | 335499 | 323582 | 3.683%
26 | 413888 | 287628 | 43.9% |  | 26 | 367233 | 328076 | 11.94% |  | 26 | 546993 | 431443 | 26.78% |  | 26 | 360720 | 323582 | 11.48%
27 | 412150 | 287628 | 43.29% |  | 27 | 360731 | 328076 | 9.953% |  | 27 | 534767 | 431443 | 23.95% |  | 27 | 356184 | 323582 | 10.08%
28 | 415124 | 287628 | 44.33% |  | 28 | 363260 | 328076 | 10.72% |  | 28 | 539309 | 431443 | 25% |  | 28 | 360626 | 323582 | 11.45%
29 | 419957 | 287628 | 46.01% |  | 29 | 368659 | 328076 | 12.37% |  | 29 | 546422 | 431443 | 26.65% |  | 29 | 364721 | 323582 | 12.71%
30 | 406637 | 287628 | 41.38% |  | 30 | 357493 | 328076 | 8.967% |  | 30 | 529667 | 431443 | 22.77% |  | 30 | 354355 | 323582 | 9.51%
31 | 253291 | 287628 | -11.94% |  | 31 | 223710 | 328076 | -31.81% |  | 31 | 332403 | 431443 | -22.96% |  | 31 | 276005 | 323582 | -14.7%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
March | Yield | Target | Variance |  | March | Yield | Target | Variance |  | March | Yield | Target | Variance |  | March | Yield | Target | Variance
1 | 979859 | 798968 | 22.64% |  | 1 | 232656 | 199742 | 16.48% |  | 1 | 1133923 | 879561 | 28.92% |  | 1 | 1242531 | 1005213 | 23.61%
2 | 930240 | 798968 | 16.43% |  | 2 | 261176 | 199742 | 30.76% |  | 2 | 1169726 | 879561 | 32.99% |  | 2 | 1283474 | 1005213 | 27.68%
3 | 895162 | 798968 | 12.04% |  | 3 | 213534 | 199742 | 6.905% |  | 3 | 951914 | 879561 | 8.226% |  | 3 | 1047376 | 1005213 | 4.194%
4 | 649984 | 798968 | -18.65% |  | 4 | 179180 | 199742 | -10.29% |  | 4 | 892243 | 879561 | 1.442% |  | 4 | 949815 | 1005213 | -5.511%
5 | 919297 | 798968 | 15.06% |  | 5 | 257535 | 199742 | 28.93% |  | 5 | 1187323 | 879561 | 34.99% |  | 5 | 1286618 | 1005213 | 27.99%
6 | 875037 | 798968 | 9.521% |  | 6 | 245649 | 199742 | 22.98% |  | 6 | 1115315 | 879561 | 26.8% |  | 6 | 1218175 | 1005213 | 21.19%
7 | 925751 | 798968 | 15.87% |  | 7 | 258414 | 199742 | 29.37% |  | 7 | 1186230 | 879561 | 34.87% |  | 7 | 1298875 | 1005213 | 29.21%
8 | 776121 | 798968 | -2.86% |  | 8 | 219608 | 199742 | 9.946% |  | 8 | 941678 | 879561 | 7.062% |  | 8 | 1040356 | 1005213 | 3.496%
9 | 181569 | 798968 | -77.27% |  | 9 | 49712 | 199742 | -75.11% |  | 9 | 160811 | 879561 | -81.72% |  | 9 | 215128 | 1005213 | -78.6%
10 | 368300 | 798968 | -53.9% |  | 10 | 102716 | 199742 | -48.58% |  | 10 | 390130 | 879561 | -55.64% |  | 10 | 454275 | 1005213 | -54.81%
11 | 224900 | 798968 | -71.85% |  | 11 | 60842 | 199742 | -69.54% |  | 11 | 256856 | 879561 | -70.8% |  | 11 | 289049 | 1005213 | -71.24%
12 | 0 | 798968 | -100% |  | 12 | 0 | 199742 | -100% |  | 12 | 0 | 879561 | -100% |  | 12 | 0 | 1005213 | -100%
13 | 431134 | 798968 | -46.04% |  | 13 | 40872 | 199742 | -79.54% |  | 13 | 214179 | 879561 | -75.65% |  | 13 | 230493 | 1005213 | -77.07%
14 | 852570 | 798968 | 6.709% |  | 14 | 233930 | 199742 | 17.12% |  | 14 | 1027271 | 879561 | 16.79% |  | 14 | 1133779 | 1005213 | 12.79%
15 | 269899 | 798968 | -66.22% |  | 15 | 73383 | 199742 | -63.26% |  | 15 | 279647 | 879561 | -68.21% |  | 15 | 325445 | 1005213 | -67.62%
16 | 884140 | 798968 | 10.66% |  | 16 | 252658 | 199742 | 26.49% |  | 16 | 978938 | 879561 | 11.3% |  | 16 | 1212739 | 1005213 | 20.64%
17 | 784121 | 798968 | -1.858% |  | 17 | 221057 | 199742 | 10.67% |  | 17 | 0 | 879561 | -100% |  | 17 | 1114950 | 1005213 | 10.92%
18 | 960221 | 798968 | 20.18% |  | 18 | 265134 | 199742 | 32.74% |  | 18 | 0 | 879561 | -100% |  | 18 | 1312671 | 1005213 | 30.59%
19 | 932964 | 798968 | 16.77% |  | 19 | 256160 | 199742 | 28.25% |  | 19 | 0 | 879561 | -100% |  | 19 | 1272194 | 1005213 | 26.56%
20 | 894395 | 798968 | 11.94% |  | 20 | 240334 | 199742 | 20.32% |  | 20 | 0 | 879561 | -100% |  | 20 | 1146569 | 1005213 | 14.06%
21 | 943645 | 798968 | 18.11% |  | 21 | 260187 | 199742 | 30.26% |  | 21 | 0 | 879561 | -100% |  | 21 | 1264725 | 1005213 | 25.82%
22 | 825457 | 798968 | 3.315% |  | 22 | 224618 | 199742 | 12.45% |  | 22 | 0 | 879561 | -100% |  | 22 | 1029170 | 1005213 | 2.383%
23 | 647000 | 798968 | -19.02% |  | 23 | 184821 | 199742 | -7.47% |  | 23 | 0 | 879561 | -100% |  | 23 | 867093 | 1005213 | -13.74%
24 | 492806 | 798968 | -38.32% |  | 24 | 133669 | 199742 | -33.08% |  | 24 | 0 | 879561 | -100% |  | 24 | 644114 | 1005213 | -35.92%
25 | 873853 | 798968 | 9.373% |  | 25 | 228267 | 199742 | 14.28% |  | 25 | 0 | 879561 | -100% |  | 25 | 1092569 | 1005213 | 8.69%
26 | 948925 | 798968 | 18.77% |  | 26 | 191182 | 199742 | -4.286% |  | 26 | 0 | 879561 | -100% |  | 26 | 865382 | 1005213 | -13.91%
27 | 931422 | 798968 | 16.58% |  | 27 | 260148 | 199742 | 30.24% |  | 27 | 0 | 879561 | -100% |  | 27 | 1194605 | 1005213 | 18.84%
28 | 940166 | 798968 | 17.67% |  | 28 | 253999 | 199742 | 27.16% |  | 28 | 0 | 879561 | -100% |  | 28 | 1187009 | 1005213 | 18.09%
29 | 950659 | 798968 | 18.99% |  | 29 | 260826 | 199742 | 30.58% |  | 29 | 0 | 879561 | -100% |  | 29 | 1213406 | 1005213 | 20.71%
30 | 922636 | 798968 | 15.48% |  | 30 | 242598 | 199742 | 21.46% |  | 30 | 0 | 879561 | -100% |  | 30 | 1126792 | 1005213 | 12.09%
31 | 574417 | 798968 | -28.11% |  | 31 | 161024 | 199742 | -19.38% |  | 31 | 0 | 879561 | -100% |  | 31 | 717017 | 1005213 | -28.67%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 9991.392
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 8779.944
| 2020-02-28 |  |  |  |  | 2020-02-28 |  | 70715.8 |  |  | 2020-02-28 |  | 66453.5 |  |  | Pl72C | 12985.259
| 2020-03-02 | 3 |  | 4866.8 |  | 2020-03-02 | 3 | 71929 | 1213.2 |  | 2020-03-02 | 3 | 67673.7 | 1220.2 |  | PL-R3 | 22786.65
| 2020-03-03 | 1 |  | 1511.2 |  | 2020-03-03 | 1 | 72305.8 | 376.8 |  | 2020-03-03 | 1 | 68052.5 | 378.8 |  | STP60 | 36693.6
| 2020-03-04 | 1 |  | 1118.8 |  | 2020-03-04 | 1 | 72584.3 | 278.5 |  | 2020-03-04 | 1 | 68333.4 | 280.9 |  | STP20-F | 6065.889
| 2020-03-05 | 1 |  | 1517.4 |  | 2020-03-05 | 1 | 72963.6 | 379.3 |  | 2020-03-05 | 1 | 68712.8 | 379.4 |  | West wing | 9465.558
| 2020-03-06 | 1 |  | 1416.2 |  | 2020-03-06 | 1 | 73316.4 | 352.8 |  | 2020-03-06 | 1 | 69068.1 | 355.3 |  | Tracker-1 | 11886.184
| 2020-03-09 | 3 |  | 3292.2 |  | 2020-03-09 | 3 | 74137.8 | 821.4 |  | 2020-03-09 | 3 | 69892.8 | 824.7 |  | Tracker-2 | 29276.394
| 2020-03-10 | 1 |  | 642.2 |  | 2020-03-10 | 1 | 74298.2 | 160.4 |  | 2020-03-10 | 1 | 70053.5 | 160.7
| 2020-03-13 | 3 |  | 670 |  | 2020-03-13 | 3 | 74464.3 | 166.1 |  | 2020-03-13 | 3 | 70222.4 | 168.9 |  | Plant total | 147930.87
| 2020-03-16 | 3 |  | 3411.2 |  | 2020-03-16 | 3 | 75319.2 | 854.9 |  | 2020-03-16 | 3 | 71073.1 | 850.7 |  | Janitza | 138203.9
| 2020-03-17 | 1 |  | 1322.8 |  | 2020-03-17 | 1 | 75648.6 | 329.4 |  | 2020-03-17 | 1 | 71405.1 | 332 |  | Difference | 9726.97
| 2020-03-18 | 1 |  | 1549.2 |  | 2020-03-18 | 1 | 76035.6 | 387 |  | 2020-03-18 | 1 | 71792.7 | 387.6 |  |  | 93.42%
| 2020-03-19 | 1 |  | 1595.4 |  | 2020-03-19 | 1 | 76433.1 | 397.5 |  | 2020-03-19 | 1 | 72192.9 | 400.2
| 2020-03-20 | 1 |  | 1492.2 |  | 2020-03-20 | 1 | 76807 | 373.9 |  | 2020-03-20 | 1 | 72565.1 | 372.2
| 2020-03-23 | 3 |  | 4064.4 |  | 2020-03-23 | 3 | 77819.6 | 1012.6 |  | 2020-03-23 | 3 | 73584.7 | 1019.6
| 2020-03-24 | 1 |  | 812.4 |  | 2020-03-24 | 1 | 78022.1 | 202.5 |  | 2020-03-24 | 1 | 73788.4 | 203.7
| 2020-03-25 | 1 |  | 1434.8 |  | 2020-03-25 | 1 | 78379.3 | 357.2 |  | 2020-03-25 | 1 | 74148.6 | 360.2
| 2020-03-31 | 5 |  | 5976.4 |  | 2020-05-04 | 40 | 90305.6 | 1490.7875 |  | 2020-05-04 | 40 | 86127.9 | 1497.4125
|  | 31 |  | 36693.6

## Apr 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
April | Yield | Target | Variance |  | April | Yield | Target | Variance |  | April | Yield | Target | Variance |  | April | Yield | Target | Variance
1 | 345377 | 264192 | 30.73% |  | 1 | 309041 | 301344 | 2.554% |  | 1 | 456981 | 396288 | 15.32% |  | 1 | 303030 | 297216 | 1.956%
2 | 417122 | 264192 | 57.89% |  | 2 | 366907 | 301344 | 21.76% |  | 2 | 544472 | 396288 | 37.39% |  | 2 | 363475 | 297216 | 22.29%
3 | 404137 | 264192 | 52.97% |  | 3 | 354149 | 301344 | 17.52% |  | 3 | 525537 | 396288 | 32.61% |  | 3 | 352212 | 297216 | 18.5%
4 | 378928 | 264192 | 43.43% |  | 4 | 332270 | 301344 | 10.26% |  | 4 | 490387 | 396288 | 23.75% |  | 4 | 360758 | 297216 | 21.38%
5 | 334992 | 264192 | 26.8% |  | 5 | 295910 | 301344 | -1.803% |  | 5 | 436911 | 396288 | 10.25% |  | 5 | 328588 | 297216 | 10.56%
6 | 318701 | 264192 | 20.63% |  | 6 | 280081 | 301344 | -7.056% |  | 6 | 411356 | 396288 | 3.802% |  | 6 | 310217 | 297216 | 4.374%
7 | 317188 | 264192 | 20.06% |  | 7 | 280667 | 301344 | -6.862% |  | 7 | 409575 | 396288 | 3.353% |  | 7 | 308065 | 297216 | 3.65%
8 | 377512 | 264192 | 42.89% |  | 8 | 333168 | 301344 | 10.56% |  | 8 | 491505 | 396288 | 24.03% |  | 8 | 360334 | 297216 | 21.24%
9 | 388152 | 264192 | 46.92% |  | 9 | 340896 | 301344 | 13.13% |  | 9 | 505886 | 396288 | 27.66% |  | 9 | 371581 | 297216 | 25.02%
10 | 254174 | 264192 | -3.792% |  | 10 | 226385 | 301344 | -24.87% |  | 10 | 331476 | 396288 | -16.35% |  | 10 | 253860 | 297216 | -14.59%
11 | 159196 | 264192 | -39.74% |  | 11 | 146521 | 301344 | -51.38% |  | 11 | 218348 | 396288 | -44.9% |  | 11 | 142024 | 297216 | -52.22%
12 | 214936 | 264192 | -18.64% |  | 12 | 189289 | 301344 | -37.19% |  | 12 | 276050 | 396288 | -30.34% |  | 12 | 215470 | 297216 | -27.5%
13 | 382260 | 264192 | 44.69% |  | 13 | 340340 | 301344 | 12.94% |  | 13 | 501786 | 396288 | 26.62% |  | 13 | 334858 | 297216 | 12.66%
14 | 360873 | 264192 | 36.59% |  | 14 | 319881 | 301344 | 6.151% |  | 14 | 471034 | 396288 | 18.86% |  | 14 | 314971 | 297216 | 5.974%
15 | 251717 | 264192 | -4.722% |  | 15 | 226321 | 301344 | -24.9% |  | 15 | 329570 | 396288 | -16.84% |  | 15 | 219946 | 297216 | -26%
16 | 316602 | 264192 | 19.84% |  | 16 | 281314 | 301344 | -6.647% |  | 16 | 412048 | 396288 | 3.977% |  | 16 | 306152 | 297216 | 3.007%
17 | 371702 | 264192 | 40.69% |  | 17 | 329047 | 301344 | 9.193% |  | 17 | 486424 | 396288 | 22.75% |  | 17 | 357068 | 297216 | 20.14%
18 | 373210 | 264192 | 41.26% |  | 18 | 330890 | 301344 | 9.805% |  | 18 | 488477 | 396288 | 23.26% |  | 18 | 325754 | 297216 | 9.602%
19 | 372304 | 264192 | 40.92% |  | 19 | 331107 | 301344 | 9.877% |  | 19 | 488198 | 396288 | 23.19% |  | 19 | 325651 | 297216 | 9.567%
20 | 365714 | 264192 | 38.43% |  | 20 | 325467 | 301344 | 8.005% |  | 20 | 479724 | 396288 | 21.05% |  | 20 | 318791 | 297216 | 7.259%
21 | 182004 | 264192 | -31.11% |  | 21 | 164827 | 301344 | -45.3% |  | 21 | 239724 | 396288 | -39.51% |  | 21 | 161749 | 297216 | -45.58%
22 | 375691 | 264192 | 42.2% |  | 22 | 335262 | 301344 | 11.26% |  | 22 | 494217 | 396288 | 24.71% |  | 22 | 327861 | 297216 | 10.31%
23 | 330844 | 264192 | 25.23% |  | 23 | 295126 | 301344 | -2.063% |  | 23 | 434804 | 396288 | 9.719% |  | 23 | 291450 | 297216 | -1.94%
24 | 109319 | 264192 | -58.62% |  | 24 | 97273 | 301344 | -67.72% |  | 24 | 142344 | 396288 | -64.08% |  | 24 | 95263 | 297216 | -67.95%
25 | 323756 | 264192 | 22.55% |  | 25 | 291002 | 301344 | -3.432% |  | 25 | 426293 | 396288 | 7.572% |  | 25 | 282752 | 297216 | -4.866%
26 | 286768 | 264192 | 8.545% |  | 26 | 256403 | 301344 | -14.91% |  | 26 | 377203 | 396288 | -4.816% |  | 26 | 252908 | 297216 | -14.91%
27 | 44724 | 264192 | -83.07% |  | 27 | 39778 | 301344 | -86.8% |  | 27 | 58315 | 396288 | -85.28% |  | 27 | 39240 | 297216 | -86.8%
28 | 130049 | 264192 | -50.77% |  | 28 | 118533 | 301344 | -60.67% |  | 28 | 171203 | 396288 | -56.8% |  | 28 | 114044 | 297216 | -61.63%
29 | 357935 | 264192 | 35.48% |  | 29 | 321377 | 301344 | 6.648% |  | 29 | 470506 | 396288 | 18.73% |  | 29 | 313654 | 297216 | 5.531%
30 | 360500 | 264192 | 36.45% |  | 30 | 324629 | 301344 | 7.727% |  | 30 | 475780 | 396288 | 20.06% |  | 30 | 315605 | 297216 | 6.187%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
April | Yield | Target | Variance |  | April | Yield | Target | Variance |  | April | Yield | Target | Variance |  | April | Yield | Target | Variance
1 | 796112 | 733867 | 8.482% |  | 1 | 160121 | 183467 | -12.72% |  | 1 | 0 | 807893 | -100% |  | 1 | 771964 | 923307 | -16.39%
2 | 945788 | 733867 | 28.88% |  | 2 | 261801 | 183467 | 42.7% |  | 2 | 61606 | 807893 | -92.37% |  | 2 | 1217319 | 923307 | 31.84%
3 | 914904 | 733867 | 24.67% |  | 3 | 251607 | 183467 | 37.14% |  | 3 | 0 | 807893 | -100% |  | 3 | 1171923 | 923307 | 26.93%
4 | 858628 | 733867 | 17% |  | 4 | 239696 | 183467 | 30.65% |  | 4 | 0 | 807893 | -100% |  | 4 | 1111203 | 923307 | 20.35%
5 | 757576 | 733867 | 3.231% |  | 5 | 199615 | 183467 | 8.802% |  | 5 | 0 | 807893 | -100% |  | 5 | 928376 | 923307 | 0.549%
6 | 716669 | 733867 | -2.343% |  | 6 | 203214 | 183467 | 10.76% |  | 6 | 0 | 807893 | -100% |  | 6 | 923910 | 923307 | 0.06531%
7 | 728169 | 733867 | -0.7764% |  | 7 | 195758 | 183467 | 6.699% |  | 7 | 0 | 807893 | -100% |  | 7 | 864949 | 923307 | -6.321%
8 | 848976 | 733867 | 15.69% |  | 8 | 238382 | 183467 | 29.93% |  | 8 | 0 | 807893 | -100% |  | 8 | 1074240 | 923307 | 16.35%
9 | 877488 | 733867 | 19.57% |  | 9 | 246040 | 183467 | 34.11% |  | 9 | 0 | 807893 | -100% |  | 9 | 1129160 | 923307 | 22.3%
10 | 569822 | 733867 | -22.35% |  | 10 | 158127 | 183467 | -13.81% |  | 10 | 0 | 807893 | -100% |  | 10 | 706041 | 923307 | -23.53%
11 | 374646 | 733867 | -48.95% |  | 11 | 78147 | 183467 | -57.41% |  | 11 | 0 | 807893 | -100% |  | 11 | 327196 | 923307 | -64.56%
12 | 478056 | 733867 | -34.86% |  | 12 | 135743 | 183467 | -26.01% |  | 12 | 0 | 807893 | -100% |  | 12 | 600351 | 923307 | -34.98%
13 | 867653 | 733867 | 18.23% |  | 13 | 198604 | 183467 | 8.251% |  | 13 | 0 | 807893 | -100% |  | 13 | 926625 | 923307 | 0.3594%
14 | 814000 | 733867 | 10.92% |  | 14 | 229335 | 183467 | 25% |  | 14 | 0 | 807893 | -100% |  | 14 | 1034192 | 923307 | 12.01%
15 | 559471 | 733867 | -23.76% |  | 15 | 155463 | 183467 | -15.26% |  | 15 | 0 | 807893 | -100% |  | 15 | 697403 | 923307 | -24.47%
16 | 708599 | 733867 | -3.443% |  | 16 | 199523 | 183467 | 8.751% |  | 16 | 0 | 807893 | -100% |  | 16 | 907568 | 923307 | -1.705%
17 | 842874 | 733867 | 14.85% |  | 17 | 225796 | 183467 | 23.07% |  | 17 | 0 | 807893 | -100% |  | 17 | 1029883 | 923307 | 11.54%
18 | 847456 | 733867 | 15.48% |  | 18 | 236971 | 183467 | 29.16% |  | 18 | 0 | 807893 | -100% |  | 18 | 1098059 | 923307 | 18.93%
19 | 846327 | 733867 | 15.32% |  | 19 | 232822 | 183467 | 26.9% |  | 19 | 0 | 807893 | -100% |  | 19 | 1034900 | 923307 | 12.09%
20 | 832740 | 733867 | 13.47% |  | 20 | 234363 | 183467 | 27.74% |  | 20 | 0 | 807893 | -100% |  | 20 | 1067442 | 923307 | 15.61%
21 | 409293 | 733867 | -44.23% |  | 21 | 115546 | 183467 | -37.02% |  | 21 | 0 | 807893 | -100% |  | 21 | 514798 | 923307 | -44.24%
22 | 852717 | 733867 | 16.2% |  | 22 | 239421 | 183467 | 30.5% |  | 22 | 0 | 807893 | -100% |  | 22 | 1096187 | 923307 | 18.72%
23 | 748267 | 733867 | 1.962% |  | 23 | 210877 | 183467 | 14.94% |  | 23 | 0 | 807893 | -100% |  | 23 | 949923 | 923307 | 2.883%
24 | 246072 | 733867 | -66.47% |  | 24 | 68525 | 183467 | -62.65% |  | 24 | 0 | 807893 | -100% |  | 24 | 294608 | 923307 | -68.09%
25 | 732912 | 733867 | -0.1301% |  | 25 | 204378 | 183467 | 11.4% |  | 25 | 0 | 807893 | -100% |  | 25 | 941023 | 923307 | 1.919%
26 | 649668 | 733867 | -11.47% |  | 26 | 179230 | 183467 | -2.309% |  | 26 | 0 | 807893 | -100% |  | 26 | 794599 | 923307 | -13.94%
27 | 101980 | 733867 | -86.1% |  | 27 | 27626 | 183467 | -84.94% |  | 27 | 0 | 807893 | -100% |  | 27 | 109471 | 923307 | -88.14%
28 | 292946 | 733867 | -60.08% |  | 28 | 81976 | 183467 | -55.32% |  | 28 | 0 | 807893 | -100% |  | 28 | 360905 | 923307 | -60.91%
29 | 810478 | 733867 | 10.44% |  | 29 | 222605 | 183467 | 21.33% |  | 29 | 0 | 807893 | -100% |  | 29 | 1025329 | 923307 | 11.05%
30 | 817965 | 733867 | 11.46% |  | 30 | 219872 | 183467 | 19.84% |  | 30 | 313616 | 807893 | -61.18% |  | 30 | 967238 | 923307 | 4.758%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 9206.387
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 8183.861
| April 2020 | 30 | 35858.4 |  |  | 2020-03-25 |  | 78379.3 |  |  | 2020-03-25 |  | 74148.6 |  |  | Pl72C | 12046.134
|  | Daily | 1195.28 |  |  | 2020-05-04 | 40 | 90305.6 | 11926.3 |  | 2020-05-04 | 40 | 86127.9 | 11979.3 |  | PL-R3 | 20848.252
[16 empty] | STP60 | 35858.4
[6 empty] | April 2020 | 30 | 8944.725 |  |  | April 2020 | 30 | 8984.475 |  |  | STP20-F | 5651.184
[7 empty] | Daily | 298.1575 |  |  |  | Daily | 299.4825 |  |  | West wing | 8367.331
[16 empty] | Tracker-1 | 375.222
[16 empty] | Tracker-2 | 25676.785
[16 empty] | Plant total | 126213.556
[16 empty] | Janitza | 106713.2
[16 empty] | Difference | 19500.356
84.55%

## May 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
May | Yield | Target | Variance |  | May | Yield | Target | Variance |  | May | Yield | Target | Variance |  | May | Yield | Target | Variance
1 | 346950 | 223711 | 55.09% |  | 1 | 311909 | 255170 | 22.24% |  | 1 | 457866 | 335566 | 36.45% |  | 1 | 303935 | 251675 | 20.76%
2 | 348688 | 223711 | 55.87% |  | 2 | 315736 | 255170 | 23.74% |  | 2 | 461964 | 335566 | 37.67% |  | 2 | 305938 | 251675 | 21.56%
3 | 175210 | 223711 | -21.68% |  | 3 | 155166 | 255170 | -39.19% |  | 3 | 225406 | 335566 | -32.83% |  | 3 | 163535 | 251675 | -35.02%
4 | 236922 | 223711 | 5.905% |  | 4 | 216817 | 255170 | -15.03% |  | 4 | 312172 | 335566 | -6.972% |  | 4 | 233524 | 251675 | -7.212%
5 | 279955 | 223711 | 25.14% |  | 5 | 252460 | 255170 | -1.062% |  | 5 | 366799 | 335566 | 9.308% |  | 5 | 183088 | 251675 | -27.25%
6 | 137906 | 223711 | -38.36% |  | 6 | 123845 | 255170 | -51.47% |  | 6 | 179242 | 335566 | -46.59% |  | 6 | 91598 | 251675 | -63.6%
7 | 209356 | 223711 | -6.417% |  | 7 | 191265 | 255170 | -25.04% |  | 7 | 276029 | 335566 | -17.74% |  | 7 | 138536 | 251675 | -44.95%
8 | 295073 | 223711 | 31.9% |  | 8 | 267621 | 255170 | 4.879% |  | 8 | 387988 | 335566 | 15.62% |  | 8 | 192381 | 251675 | -23.56%
9 | 304535 | 223711 | 36.13% |  | 9 | 275663 | 255170 | 8.031% |  | 9 | 402169 | 335566 | 19.85% |  | 9 | 201710 | 251675 | -19.85%
10 | 330695 | 223711 | 47.82% |  | 10 | 301419 | 255170 | 18.12% |  | 10 | 437194 | 335566 | 30.29% |  | 10 | 216926 | 251675 | -13.81%
11 | 222335 | 223711 | -0.6151% |  | 11 | 205550 | 255170 | -19.45% |  | 11 | 291825 | 335566 | -13.03% |  | 11 | 146966 | 251675 | -41.6%
12 | 203530 | 223711 | -9.021% |  | 12 | 183092 | 255170 | -28.25% |  | 12 | 266423 | 335566 | -20.6% |  | 12 | 133593 | 251675 | -46.92%
13 | 306919 | 223711 | 37.19% |  | 13 | 278132 | 255170 | 8.999% |  | 13 | 403504 | 335566 | 20.25% |  | 13 | 202548 | 251675 | -19.52%
14 | 320943 | 223711 | 43.46% |  | 14 | 293712 | 255170 | 15.1% |  | 14 | 424552 | 335566 | 26.52% |  | 14 | 210898 | 251675 | -16.2%
15 | 329060 | 223711 | 47.09% |  | 15 | 300207 | 255170 | 17.65% |  | 15 | 435146 | 335566 | 29.68% |  | 15 | 217054 | 251675 | -13.76%
16 | 324830 | 223711 | 45.2% |  | 16 | 296763 | 255170 | 16.3% |  | 16 | 429185 | 335566 | 27.9% |  | 16 | 213655 | 251675 | -15.11%
17 | 309998 | 223711 | 38.57% |  | 17 | 283761 | 255170 | 11.2% |  | 17 | 411405 | 335566 | 22.6% |  | 17 | 204125 | 251675 | -18.89%
18 | 279620 | 223711 | 24.99% |  | 18 | 256388 | 255170 | 0.4773% |  | 18 | 369066 | 335566 | 9.983% |  | 18 | 183245 | 251675 | -27.19%
19 | 288802 | 223711 | 29.1% |  | 19 | 261446 | 255170 | 2.46% |  | 19 | 379358 | 335566 | 13.05% |  | 19 | 189274 | 251675 | -24.79%
20 | 295673 | 223711 | 32.17% |  | 20 | 266926 | 255170 | 4.607% |  | 20 | 387222 | 335566 | 15.39% |  | 20 | 193561 | 251675 | -23.09%
21 | 255973 | 223711 | 14.42% |  | 21 | 234472 | 255170 | -8.111% |  | 21 | 335999 | 335566 | 0.129% |  | 21 | 169893 | 251675 | -32.5%
22 | 289905 | 223711 | 29.59% |  | 22 | 266523 | 255170 | 4.449% |  | 22 | 382085 | 335566 | 13.86% |  | 22 | 191174 | 251675 | -24.04%
23 | 302873 | 223711 | 35.39% |  | 23 | 279377 | 255170 | 9.487% |  | 23 | 400102 | 335566 | 19.23% |  | 23 | 199422 | 251675 | -20.76%
24 | 297795 | 223711 | 33.12% |  | 24 | 274788 | 255170 | 7.688% |  | 24 | 393062 | 335566 | 17.13% |  | 24 | 196451 | 251675 | -21.94%
25 | 204551 | 223711 | -8.565% |  | 25 | 186055 | 255170 | -27.09% |  | 25 | 268168 | 335566 | -20.08% |  | 25 | 133553 | 251675 | -46.93%
26 | 97881 | 223711 | -56.25% |  | 26 | 87391 | 255170 | -65.75% |  | 26 | 127121 | 335566 | -62.12% |  | 26 | 63553 | 251675 | -74.75%
27 | 237968 | 223711 | 6.373% |  | 27 | 225241 | 255170 | -11.73% |  | 27 | 315498 | 335566 | -5.98% |  | 27 | 172423 | 251675 | -31.49%
28 | 221558 | 223711 | -0.9624% |  | 28 | 200671 | 255170 | -21.36% |  | 28 | 290120 | 335566 | -13.54% |  | 28 | 194647 | 251675 | -22.66%
29 | 71134 | 223711 | -68.2% |  | 29 | 64176 | 255170 | -74.85% |  | 29 | 92985 | 335566 | -72.29% |  | 29 | 62146 | 251675 | -75.31%
30 | 271133 | 223711 | 21.2% |  | 30 | 244350 | 255170 | -4.24% |  | 30 | 356510 | 335566 | 6.241% |  | 30 | 235892 | 251675 | -6.271%
31 | 297901 | 223711 | 33.16% |  | 31 | 278042 | 255170 | 8.963% |  | 31 | 394173 | 335566 | 17.47% |  | 31 | 260427 | 251675 | 3.478%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
May | Yield | Target | Variance |  | May | Yield | Target | Variance |  | May | Yield | Target | Variance |  | May | Yield | Target | Variance
1 | 788194 | 621419 | 26.84% |  | 1 | 221652 | 155355 | 42.67% |  | 1 | 824558 | 684103 | 20.53% |  | 1 | 923648 | 781832 | 18.14%
2 | 793775 | 621419 | 27.74% |  | 2 | 193769 | 155355 | 24.73% |  | 2 | 749126 | 684103 | 9.505% |  | 2 | 829035 | 781832 | 6.037%
3 | 393248 | 621419 | -36.72% |  | 3 | 114619 | 155355 | -26.22% |  | 3 | 376357 | 684103 | -44.99% |  | 3 | 433328 | 781832 | -44.58%
4 | 523453 | 621419 | -15.76% |  | 4 | 151248 | 155355 | -2.644% |  | 4 | 571908 | 684103 | -16.4% |  | 4 | 637921 | 781832 | -18.41%
5 | 621671 | 621419 | 0.04055% |  | 5 | 177173 | 155355 | 14.04% |  | 5 | 638058 | 684103 | -6.731% |  | 5 | 738233 | 781832 | -5.577%
6 | 306948 | 621419 | -50.61% |  | 6 | 87447 | 155355 | -43.71% |  | 6 | 255840 | 684103 | -62.6% |  | 6 | 344131 | 781832 | -55.98%
7 | 467024 | 621419 | -24.85% |  | 7 | 133475 | 155355 | -14.08% |  | 7 | 471957 | 684103 | -31.01% |  | 7 | 564359 | 781832 | -27.82%
8 | 659167 | 621419 | 6.074% |  | 8 | 189169 | 155355 | 21.77% |  | 8 | 709846 | 684103 | 3.763% |  | 8 | 799384 | 781832 | 2.245%
9 | 688799 | 621419 | 10.84% |  | 9 | 183386 | 155355 | 18.04% |  | 9 | 657948 | 684103 | -3.823% |  | 9 | 765787 | 781832 | -2.052%
10 | 746072 | 621419 | 20.06% |  | 10 | 206198 | 155355 | 32.73% |  | 10 | 769864 | 684103 | 12.54% |  | 10 | 870532 | 781832 | 11.35%
11 | 491093 | 621419 | -20.97% |  | 11 | 139141 | 155355 | -10.44% |  | 11 | 484674 | 684103 | -29.15% |  | 11 | 567703 | 781832 | -27.39%
12 | 449474 | 621419 | -27.67% |  | 12 | 123269 | 155355 | -20.65% |  | 12 | 504550 | 684103 | -26.25% |  | 12 | 494469 | 781832 | -36.76%
13 | 685557 | 621419 | 10.32% |  | 13 | 196457 | 155355 | 26.46% |  | 13 | 820866 | 684103 | 19.99% |  | 13 | 811969 | 781832 | 3.855%
14 | 721359 | 621419 | 16.08% |  | 14 | 204982 | 155355 | 31.94% |  | 14 | 880537 | 684103 | 28.71% |  | 14 | 870813 | 781832 | 11.38%
15 | 736225 | 621419 | 18.47% |  | 15 | 210528 | 155355 | 35.51% |  | 15 | 854431 | 684103 | 24.9% |  | 15 | 864793 | 781832 | 10.61%
16 | 729180 | 621419 | 17.34% |  | 16 | 206401 | 155355 | 32.86% |  | 16 | 903574 | 684103 | 32.08% |  | 16 | 869624 | 781832 | 11.23%
17 | 694057 | 621419 | 11.69% |  | 17 | 198783 | 155355 | 27.95% |  | 17 | 832240 | 684103 | 21.65% |  | 17 | 837460 | 781832 | 7.115%
18 | 622637 | 621419 | 0.196% |  | 18 | 178023 | 155355 | 14.59% |  | 18 | 769854 | 684103 | 12.53% |  | 18 | 756224 | 781832 | -3.275%
19 | 651920 | 621419 | 4.908% |  | 19 | 178315 | 155355 | 14.78% |  | 19 | 734680 | 684103 | 7.393% |  | 19 | 738939 | 781832 | -5.486%
20 | 659982 | 621419 | 6.206% |  | 20 | 172911 | 155355 | 11.3% |  | 20 | 738412 | 684103 | 7.939% |  | 20 | 727189 | 781832 | -6.989%
21 | 561022 | 621419 | -9.719% |  | 21 | 161949 | 155355 | 4.244% |  | 21 | 690082 | 684103 | 0.874% |  | 21 | 656464 | 781832 | -16.04%
22 | 643549 | 621419 | 3.561% |  | 22 | 184361 | 155355 | 18.67% |  | 22 | 807179 | 684103 | 17.99% |  | 22 | 785341 | 781832 | 0.4488%
23 | 673051 | 621419 | 8.309% |  | 23 | 186049 | 155355 | 19.76% |  | 23 | 818916 | 684103 | 19.71% |  | 23 | 788729 | 781832 | 0.8822%
24 | 661173 | 621419 | 6.397% |  | 24 | 183323 | 155355 | 18% |  | 24 | 818339 | 684103 | 19.62% |  | 24 | 789795 | 781832 | 1.019%
25 | 445036 | 621419 | -28.38% |  | 25 | 129307 | 155355 | -16.77% |  | 25 | 487882 | 684103 | -28.68% |  | 25 | 465613 | 781832 | -40.45%
26 | 219409 | 621419 | -64.69% |  | 26 | 61991 | 155355 | -60.1% |  | 26 | 242312 | 684103 | -64.58% |  | 26 | 238654 | 781832 | -69.48%
27 | 523088 | 621419 | -15.82% |  | 27 | 152459 | 155355 | -1.864% |  | 27 | 696816 | 684103 | 1.858% |  | 27 | 677005 | 781832 | -13.41%
28 | 492850 | 621419 | -20.69% |  | 28 | 141479 | 155355 | -8.932% |  | 28 | 588106 | 684103 | -14.03% |  | 28 | 599152 | 781832 | -23.37%
29 | 159457 | 621419 | -74.34% |  | 29 | 44892 | 155355 | -71.1% |  | 29 | 173317 | 684103 | -74.67% |  | 29 | 194329 | 781832 | -75.14%
30 | 596284 | 621419 | -4.045% |  | 30 | 166087 | 155355 | 6.908% |  | 30 | 744678 | 684103 | 8.855% |  | 30 | 732785 | 781832 | -6.273%
31 | 655164 | 621419 | 5.43% |  | 31 | 177882 | 155355 | 14.5% |  | 31 | 866119 | 684103 | 26.61% |  | 31 | 779442 | 781832 | -0.3057%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 8095.672
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 7378.964
| 2020-03-25 |  |  |  |  | 2020-03-25 |  | 78379.3 |  |  | 2020-03-25 |  | 74148.6 |  |  | Pl72C | 10660.338
| 2020-05-04 | 40 |  | 4781.12 |  | 2020-05-04 | 40 | 90305.6 | 1192.63 |  | 2020-05-04 | 40 | 86127.9 | 1197.93 |  | PL-R3 | 18059.918
| 2020-05-05 | 1 |  | 1064.4 |  | 2020-05-05 | 1 | 90571.3 | 265.7 |  | 2020-05-05 | 1 | 86394.4 | 266.5 |  | STP60 | 31416.87
| 2020-05-06 | 1 |  | 560.8 |  | 2020-05-06 | 1 | 90711.4 | 140.1 |  | 2020-05-06 | 1 | 86534.7 | 140.3 |  | STP20-F | 5056.725
| 2020-05-07 | 1 |  | 788.8 |  | 2020-05-07 | 1 | 90908.1 | 196.7 |  | 2020-05-07 | 1 | 86732.4 | 197.7 |  | West wing | 5805.671
| 2020-05-08 | 1 |  | 1074.4 |  | 2020-05-08 | 1 | 91175.7 | 267.6 |  | 2020-05-08 | 1 | 87002 | 269.6 |  | Tracker-1 | 20483.026
| 2020-05-11 | 3 |  | 3307.8 |  | 2020-05-11 | 3 | 92002 | 826.3 |  | 2020-05-11 | 3 | 87829.6 | 827.6 |  | Tracker-2 | 21152.85
| 2020-05-12 | 1 |  | 778.6 |  | 2020-05-12 | 1 | 92196.3 | 194.3 |  | 2020-05-12 | 1 | 88024.6 | 195
| 2020-05-13 | 1 |  | 1181.4 |  | 2020-05-13 | 1 | 92491.3 | 295 |  | 2020-05-13 | 1 | 88320.3 | 295.7 |  | Plant total | 128110.034
| 2020-05-14 | 1 |  | 1199.8 |  | 2020-05-14 | 1 | 92791.2 | 299.9 |  | 2020-05-14 | 1 | 88620.3 | 300 |  | Janitza | 102336.6
| 2020-05-15 | 1 |  | 1215.6 |  | 2020-05-15 | 1 | 93094.6 | 303.4 |  | 2020-05-15 | 1 | 88924.7 | 304.4 |  | Difference | 25773.434
| 2020-05-18 | 3 |  | 3475.4 |  | 2020-05-18 | 3 | 93962.6 | 868 |  | 2020-05-18 | 3 | 89794.4 | 869.7 |  |  | 79.88%
| 2020-05-19 | 1 |  | 1126.8 |  | 2020-05-19 | 1 | 94243.8 | 281.2 |  | 2020-05-19 | 1 | 90076.6 | 282.2
| 2020-05-20 | 1 |  | 1090.8 |  | 2020-05-20 | 1 | 94515.6 | 271.8 |  | 2020-05-20 | 1 | 90350.2 | 273.6
| 2020-05-21 | 1 |  | 980.6 |  | 2020-05-21 | 1 | 94760.9 | 245.3 |  | 2020-05-21 | 1 | 90595.2 | 245
| 2020-05-22 | 1 |  | 1044.6 |  | 2020-05-22 | 1 | 95021.8 | 260.9 |  | 2020-05-22 | 1 | 90856.6 | 261.4
| 2020-05-25 | 3 |  | 3091.8 |  | 2020-05-25 | 3 | 95794.2 | 772.4 |  | 2020-05-25 | 3 | 91630.1 | 773.5
| 2020-05-26 | 1 |  | 356.6 |  | 2020-05-26 | 1 | 95883 | 88.8 |  | 2020-05-26 | 1 | 91719.6 | 89.5
| 2020-05-27 | 1 |  | 861.2 |  | 2020-05-27 | 1 | 96098.6 | 215.6 |  | 2020-05-27 | 1 | 91934.6 | 215
| 2020-05-28 | 1 |  | 877.2 |  | 2020-05-28 | 1 | 96317.4 | 218.8 |  | 2020-05-28 | 1 | 92154.4 | 219.8
| 2020-06-01 | 4 |  | 2559.15 |  | 2020-06-01 | 4 | 97170 | 639.45 |  | 2020-06-01 | 4 | 93007.9 | 640.125
|  |  |  | 31416.87 |  |  |  |  | 7843.88 |  |  |  |  | 7864.555

## Jun 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
June | Yield | Target | Variance |  | June | Yield | Target | Variance |  | June | Yield | Target | Variance |  | June | Yield | Target | Variance
1 | 269168 | 198144 | 35.84% |  | 1 | 246558 | 226008 | 9.093% |  | 1 | 353836 | 297216 | 19.05% |  | 1 | 235524 | 222912 | 5.658%
2 | 187934 | 198144 | -5.153% |  | 2 | 176894 | 226008 | -21.73% |  | 2 | 248178 | 297216 | -16.5% |  | 2 | 165181 | 222912 | -25.9%
3 | 236957 | 198144 | 19.59% |  | 3 | 217687 | 226008 | -3.682% |  | 3 | 311333 | 297216 | 4.75% |  | 3 | 206525 | 222912 | -7.351%
4 | 178953 | 198144 | -9.685% |  | 4 | 163528 | 226008 | -27.65% |  | 4 | 234306 | 297216 | -21.17% |  | 4 | 155854 | 222912 | -30.08%
5 | 280568 | 198144 | 41.6% |  | 5 | 261792 | 226008 | 15.83% |  | 5 | 369318 | 297216 | 24.26% |  | 5 | 245336 | 222912 | 10.06%
6 | 222249 | 198144 | 12.17% |  | 6 | 212471 | 226008 | -5.99% |  | 6 | 295289 | 297216 | -0.6484% |  | 6 | 195136 | 222912 | -12.46%
7 | 227694 | 198144 | 14.91% |  | 7 | 211733 | 226008 | -6.316% |  | 7 | 299812 | 297216 | 0.8734% |  | 7 | 199067 | 222912 | -10.7%
8 | 279640 | 198144 | 41.13% |  | 8 | 261585 | 226008 | 15.74% |  | 8 | 368821 | 297216 | 24.09% |  | 8 | 244813 | 222912 | 9.825%
9 | 265563 | 198144 | 34.03% |  | 9 | 248946 | 226008 | 10.15% |  | 9 | 349708 | 297216 | 17.66% |  | 9 | 232358 | 222912 | 4.238%
10 | 267928 | 198144 | 35.22% |  | 10 | 251845 | 226008 | 11.43% |  | 10 | 353838 | 297216 | 19.05% |  | 10 | 234635 | 222912 | 5.259%
11 | 280720 | 198144 | 41.67% |  | 11 | 265885 | 226008 | 17.64% |  | 11 | 372109 | 297216 | 25.2% |  | 11 | 246432 | 222912 | 10.55%
12 | 218866 | 198144 | 10.46% |  | 12 | 205248 | 226008 | -9.186% |  | 12 | 289480 | 297216 | -2.603% |  | 12 | 191816 | 222912 | -13.95%
13 | 287704 | 198144 | 45.2% |  | 13 | 270281 | 226008 | 19.59% |  | 13 | 380209 | 297216 | 27.92% |  | 13 | 251662 | 222912 | 12.9%
14 | 289013 | 198144 | 45.86% |  | 14 | 269470 | 226008 | 19.23% |  | 14 | 382289 | 297216 | 28.62% |  | 14 | 252811 | 222912 | 13.41%
15 | 220021 | 198144 | 11.04% |  | 15 | 204399 | 226008 | -9.561% |  | 15 | 291720 | 297216 | -1.849% |  | 15 | 192740 | 222912 | -13.54%
16 | 285329 | 198144 | 44% |  | 16 | 268811 | 226008 | 18.94% |  | 16 | 377187 | 297216 | 26.91% |  | 16 | 249791 | 222912 | 12.06%
17 | 286856 | 198144 | 44.77% |  | 17 | 269679 | 226008 | 19.32% |  | 17 | 378665 | 297216 | 27.4% |  | 17 | 251256 | 222912 | 12.72%
18 | 0 | 198144 | -100% |  | 18 | 0 | 226008 | -100% |  | 18 | 0 | 297216 | -100% |  | 18 | 0 | 222912 | -100%
19 | 280907 | 198144 | 41.77% |  | 19 | 265569 | 226008 | 17.5% |  | 19 | 371226 | 297216 | 24.9% |  | 19 | 246574 | 222912 | 10.61%
20 | 242258 | 198144 | 22.26% |  | 20 | 226046 | 226008 | 0.01681% |  | 20 | 321586 | 297216 | 8.199% |  | 20 | 212390 | 222912 | -4.72%
21 | 277840 | 198144 | 40.22% |  | 21 | 261597 | 226008 | 15.75% |  | 21 | 367554 | 297216 | 23.67% |  | 21 | 243186 | 222912 | 9.095%
22 | 263947 | 198144 | 33.21% |  | 22 | 249137 | 226008 | 10.23% |  | 22 | 348259 | 297216 | 17.17% |  | 22 | 231299 | 222912 | 3.762%
23 | 286050 | 198144 | 44.36% |  | 23 | 270579 | 226008 | 19.72% |  | 23 | 379319 | 297216 | 27.62% |  | 23 | 250456 | 222912 | 12.36%
24 | 285008 | 198144 | 43.84% |  | 24 | 269088 | 226008 | 19.06% |  | 24 | 375967 | 297216 | 26.5% |  | 24 | 249601 | 222912 | 11.97%
25 | 272516 | 198144 | 37.53% |  | 25 | 255892 | 226008 | 13.22% |  | 25 | 359113 | 297216 | 20.83% |  | 25 | 238654 | 222912 | 7.062%
26 | 228618 | 198144 | 15.38% |  | 26 | 217705 | 226008 | -3.674% |  | 26 | 300796 | 297216 | 1.205% |  | 26 | 200853 | 222912 | -9.896%
27 | 286887 | 198144 | 44.79% |  | 27 | 268448 | 226008 | 18.78% |  | 27 | 378805 | 297216 | 27.45% |  | 27 | 251230 | 222912 | 12.7%
28 | 185536 | 198144 | -6.363% |  | 28 | 171585 | 226008 | -24.08% |  | 28 | 245536 | 297216 | -17.39% |  | 28 | 161578 | 222912 | -27.51%
29 | 239337 | 198144 | 20.79% |  | 29 | 224128 | 226008 | -0.8318% |  | 29 | 318615 | 297216 | 7.2% |  | 29 | 210451 | 222912 | -5.59%
30 | 277427 | 198144 | 40.01% |  | 30 | 260327 | 226008 | 15.18% |  | 30 | 365035 | 297216 | 22.82% |  | 30 | 242877 | 222912 | 8.956%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
June | Yield | Target | Variance |  | June | Yield | Target | Variance |  | June | Yield | Target | Variance |  | June | Yield | Target | Variance
1 | 596240 | 550400 | 8.328% |  | 1 | 171425 | 137600 | 24.58% |  | 1 | 785421 | 605920 | 29.62% |  | 1 | 718031 | 692480 | 3.69%
2 | 401906 | 550400 | -26.98% |  | 2 | 119436 | 137600 | -13.2% |  | 2 | 559841 | 605920 | -7.605% |  | 2 | 514802 | 692480 | -25.66%
3 | 516446 | 550400 | -6.169% |  | 3 | 150188 | 137600 | 9.148% |  | 3 | 689205 | 605920 | 13.75% |  | 3 | 633700 | 692480 | -8.488%
4 | 395112 | 550400 | -28.21% |  | 4 | 113015 | 137600 | -17.87% |  | 4 | 498818 | 605920 | -17.68% |  | 4 | 464915 | 692480 | -32.86%
5 | 616510 | 550400 | 12.01% |  | 5 | 177891 | 137600 | 29.28% |  | 5 | 856437 | 605920 | 41.34% |  | 5 | 777526 | 692480 | 12.28%
6 | 482642 | 550400 | -12.31% |  | 6 | 140897 | 137600 | 2.396% |  | 6 | 694755 | 605920 | 14.66% |  | 6 | 627955 | 692480 | -9.318%
7 | 494470 | 550400 | -10.16% |  | 7 | 144859 | 137600 | 5.275% |  | 7 | 678214 | 605920 | 11.93% |  | 7 | 619687 | 692480 | -10.51%
8 | 608429 | 550400 | 10.54% |  | 8 | 177146 | 137600 | 28.74% |  | 8 | 862238 | 605920 | 42.3% |  | 8 | 780361 | 692480 | 12.69%
9 | 582448 | 550400 | 5.823% |  | 9 | 168045 | 137600 | 22.13% |  | 9 | 809272 | 605920 | 33.56% |  | 9 | 733863 | 692480 | 5.976%
10 | 588103 | 550400 | 6.85% |  | 10 | 168724 | 137600 | 22.62% |  | 10 | 819517 | 605920 | 35.25% |  | 10 | 739651 | 692480 | 6.812%
11 | 612475 | 550400 | 11.28% |  | 11 | 179206 | 137600 | 30.24% |  | 11 | 845600 | 605920 | 39.56% |  | 11 | 753750 | 692480 | 8.848%
12 | 468373 | 550400 | -14.9% |  | 12 | 139296 | 137600 | 1.233% |  | 12 | 659743 | 605920 | 8.883% |  | 12 | 600879 | 692480 | -13.23%
13 | 628731 | 550400 | 14.23% |  | 13 | 182769 | 137600 | 32.83% |  | 13 | 899939 | 605920 | 48.52% |  | 13 | 809918 | 692480 | 16.96%
14 | 637184 | 550400 | 15.77% |  | 14 | 183949 | 137600 | 33.68% |  | 14 | 887579 | 605920 | 46.48% |  | 14 | 804163 | 692480 | 16.13%
15 | 491288 | 550400 | -10.74% |  | 15 | 141052 | 137600 | 2.509% |  | 15 | 641061 | 605920 | 5.8% |  | 15 | 594242 | 692480 | -14.19%
16 | 621349 | 550400 | 12.89% |  | 16 | 180221 | 137600 | 30.97% |  | 16 | 887237 | 605920 | 46.43% |  | 16 | 800601 | 692480 | 15.61%
17 | 626874 | 550400 | 13.89% |  | 17 | 182038 | 137600 | 32.3% |  | 17 | 895729 | 605920 | 47.83% |  | 17 | 808509 | 692480 | 16.76%
18 | 0 | 550400 | -100% |  | 18 | 0 | 137600 | -100% |  | 18 | 0 | 605920 | -100% |  | 18 | 0 | 692480 | -100%
19 | 607630 | 550400 | 10.4% |  | 19 | 141434 | 137600 | 2.786% |  | 19 | 662553 | 605920 | 9.347% |  | 19 | 676782 | 692480 | -2.267%
20 | 535927 | 550400 | -2.63% |  | 20 | 154541 | 137600 | 12.31% |  | 20 | 721607 | 605920 | 19.09% |  | 20 | 737352 | 692480 | 6.48%
21 | 608187 | 550400 | 10.5% |  | 21 | 176679 | 137600 | 28.4% |  | 21 | 869819 | 605920 | 43.55% |  | 21 | 893166 | 692480 | 28.98%
22 | 571997 | 550400 | 3.924% |  | 22 | 168014 | 137600 | 22.1% |  | 22 | 833244 | 605920 | 37.52% |  | 22 | 856067 | 692480 | 23.62%
23 | 623339 | 550400 | 13.25% |  | 23 | 177744 | 137600 | 29.17% |  | 23 | 859441 | 605920 | 41.84% |  | 23 | 887372 | 692480 | 28.14%
24 | 617439 | 550400 | 12.18% |  | 24 | 179988 | 137600 | 30.81% |  | 24 | 889369 | 605920 | 46.78% |  | 24 | 914569 | 692480 | 32.07%
25 | 591706 | 550400 | 7.505% |  | 25 | 170636 | 137600 | 24.01% |  | 25 | 832590 | 605920 | 37.41% |  | 25 | 859495 | 692480 | 24.12%
26 | 491658 | 550400 | -10.67% |  | 26 | 147167 | 137600 | 6.953% |  | 26 | 730744 | 605920 | 20.6% |  | 26 | 765465 | 692480 | 10.54%
27 | 630872 | 550400 | 14.62% |  | 27 | 182366 | 137600 | 32.53% |  | 27 | 878877 | 605920 | 45.05% |  | 27 | 916768 | 692480 | 32.39%
28 | 410057 | 550400 | -25.5% |  | 28 | 118853 | 137600 | -13.62% |  | 28 | 530565 | 605920 | -12.44% |  | 28 | 577555 | 692480 | -16.6%
29 | 530776 | 550400 | -3.565% |  | 29 | 151862 | 137600 | 10.36% |  | 29 | 713115 | 605920 | 17.69% |  | 29 | 743224 | 692480 | 7.328%
30 | 609263 | 550400 | 10.69% |  | 30 | 175836 | 137600 | 27.79% |  | 30 | 854566 | 605920 | 41.04% |  | 30 | 883870 | 692480 | 27.64%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 7411.494
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 6946.913
| 2020-06-01 | 1 |  | 848.05 |  | 2020-06-01 | 1 |  | 213.15 |  | 2020-06-01 | 1 |  | 210.875 |  | Pl72C | 9787.909
| 2020-06-02 | 1 |  | 648.8 |  | 2020-06-02 | 1 |  | 162.4 |  | 2020-06-02 | 1 |  | 162 |  | PL-R3 | 15601.191
| 2020-06-03 | 1 |  | 938.4 |  | 2020-06-03 | 1 |  | 235.1 |  | 2020-06-03 | 1 |  | 234.1 |  | STP60 | 28725.05
| 2020-06-04 | 1 |  | 678.2 |  | 2020-06-04 | 1 |  | 169.1 |  | 2020-06-04 | 1 |  | 170 |  | STP20-F | 4493.852
| 2020-06-05 | 1 |  | 519 |  | 2020-06-05 | 1 |  | 131.5 |  | 2020-06-05 | 1 |  | 128 |  | West wing | 6490.086
| 2020-06-08 | 3 |  | 2923.8 |  | 2020-06-08 | 3 |  | 730.5 |  | 2020-06-08 | 3 |  | 731.4 |  | Tracker-1 | 21561.675
| 2020-06-09 | 1 |  | 1277.6 |  | 2020-06-09 | 1 |  | 318.9 |  | 2020-06-09 | 1 |  | 319.9 |  | Tracker-2 | 20776.207
| 2020-06-10 | 1 |  | 1086 |  | 2020-06-10 | 1 |  | 271.7 |  | 2020-06-10 | 1 |  | 271.3
| 2020-06-11 | 1 |  | 1049.2 |  | 2020-06-11 | 1 |  | 262.5 |  | 2020-06-11 | 1 |  | 262.1 |  |  | kWh | Value
| 2020-06-12 | 1 |  | 825.4 |  | 2020-06-12 | 1 |  | 206.5 |  | 2020-06-12 | 1 |  | 206.2 |  | Plant total | 121794.377 | 207050.4409
| 2020-06-15 | 3 |  | 3014.6 |  | 2020-06-15 | 3 |  | 754.2 |  | 2020-06-15 | 3 |  | 753.1 |  | Janitza | 103720 | 176324
| 2020-06-17 | 2 |  | 2143.6 |  | 2020-06-17 | 2 |  | 536.1 |  | 2020-06-17 | 2 |  | 535.7 |  | Difference | 18074.377 | 30726.4409
| 2020-06-18 | 1 |  | 992.8 |  | 2020-06-18 | 1 |  | 248.5 |  | 2020-06-18 | 1 |  | 247.9 |  |  | 85.16% | 85.16%
| 2020-06-19 | 1 |  | 1065.6 |  | 2020-06-19 | 1 |  | 266.6 |  | 2020-06-19 | 1 |  | 266.2
| 2020-06-22 | 3 |  | 2946.2 |  | 2020-06-22 | 3 |  | 736.8 |  | 2020-06-22 | 3 |  | 736.3
| 2020-06-23 | 1 |  | 1081.8 |  | 2020-06-23 | 1 |  | 270.3 |  | 2020-06-23 | 1 |  | 270.6
| 2020-06-24 | 1 |  | 1081.6 |  | 2020-06-24 | 1 |  | 270.3 |  | 2020-06-24 | 1 |  | 270.5
| 2020-06-25 | 1 |  | 994.2 |  | 2020-06-25 | 1 |  | 254.7 |  | 2020-06-25 | 1 |  | 242.4
| 2020-06-26 | 1 |  | 855 |  | 2020-06-26 | 1 |  | 214.1 |  | 2020-06-26 | 1 |  | 213.4
| 2020-06-30 | 4 |  | 3755.2 |  | 2020-06-30 | 4 |  | 938.7 |  | 2020-06-30 | 4 |  | 938.9
|  | 30 |  | 28725.05 |  |  | 30 |  | 7191.65 |  |  | 30 |  | 7170.875

## Jul 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
July | Yield | Target | Variance |  | July | Yield | Target | Variance |  | July | Yield | Target | Variance |  | July | Yield | Target | Variance
1 | 290776 | 223711 | 29.98% |  | 1 | 273753 | 255170 | 7.283% |  | 1 | 384434 | 335566 | 14.56% |  | 1 | 254484 | 251675 | 1.116%
2 | 292854 | 223711 | 30.91% |  | 2 | 274999 | 255170 | 7.771% |  | 2 | 387566 | 335566 | 15.5% |  | 2 | 256245 | 251675 | 1.816%
3 | 275200 | 223711 | 23.02% |  | 3 | 255967 | 255170 | 0.3123% |  | 3 | 364182 | 335566 | 8.528% |  | 3 | 240091 | 251675 | -4.603%
4 | 270286 | 223711 | 20.82% |  | 4 | 247077 | 255170 | -3.172% |  | 4 | 355770 | 335566 | 6.021% |  | 4 | 235212 | 251675 | -6.541%
5 | 291755 | 223711 | 30.42% |  | 5 | 273503 | 255170 | 7.185% |  | 5 | 387012 | 335566 | 15.33% |  | 5 | 255535 | 251675 | 1.534%
6 | 296600 | 223711 | 32.58% |  | 6 | 277418 | 255170 | 8.719% |  | 6 | 391298 | 335566 | 16.61% |  | 6 | 259674 | 251675 | 3.178%
7 | 246759 | 223711 | 10.3% |  | 7 | 227310 | 255170 | -10.92% |  | 7 | 323099 | 335566 | -3.715% |  | 7 | 215904 | 251675 | -14.21%
8 | 280757 | 223711 | 25.5% |  | 8 | 260812 | 255170 | 2.211% |  | 8 | 369841 | 335566 | 10.21% |  | 8 | 245205 | 251675 | -2.571%
9 | 107058 | 223711 | -52.14% |  | 9 | 79393 | 255170 | -68.89% |  | 9 | 139860 | 335566 | -58.32% |  | 9 | 93382 | 251675 | -62.9%
10 | 225949 | 223711 | 1% |  | 10 | 230654 | 255170 | -9.608% |  | 10 | 295820 | 335566 | -11.84% |  | 10 | 197845 | 251675 | -21.39%
11 | 117554 | 223711 | -47.45% |  | 11 | 123419 | 255170 | -51.63% |  | 11 | 154037 | 335566 | -54.1% |  | 11 | 104530 | 251675 | -58.47%
12 | 312337 | 223711 | 39.62% |  | 12 | 325815 | 255170 | 27.69% |  | 12 | 412204 | 335566 | 22.84% |  | 12 | 273671 | 251675 | 8.74%
13 | 208522 | 223711 | -6.79% |  | 13 | 215748 | 255170 | -15.45% |  | 13 | 269836 | 335566 | -19.59% |  | 13 | 183247 | 251675 | -27.19%
14 | 27365 | 223711 | -87.77% |  | 14 | 27651 | 255170 | -89.16% |  | 14 | 35563 | 335566 | -89.4% |  | 14 | 23931 | 251675 | -90.49%
15 | 309418 | 223711 | 38.31% |  | 15 | 320864 | 255170 | 25.75% |  | 15 | 407931 | 335566 | 21.57% |  | 15 | 270056 | 251675 | 7.303%
16 | 215574 | 223711 | -3.637% |  | 16 | 229305 | 255170 | -10.14% |  | 16 | 287696 | 335566 | -14.27% |  | 16 | 189525 | 251675 | -24.69%
17 | 314979 | 223711 | 40.8% |  | 17 | 326137 | 255170 | 27.81% |  | 17 | 415972 | 335566 | 23.96% |  | 17 | 274714 | 251675 | 9.154%
18 | 312940 | 223711 | 39.89% |  | 18 | 323720 | 255170 | 26.86% |  | 18 | 413367 | 335566 | 23.19% |  | 18 | 272625 | 251675 | 8.324%
19 | 296880 | 223711 | 32.71% |  | 19 | 306164 | 255170 | 19.98% |  | 19 | 390167 | 335566 | 16.27% |  | 19 | 258774 | 251675 | 2.821%
20 | 306318 | 223711 | 36.93% |  | 20 | 314596 | 255170 | 23.29% |  | 20 | 403120 | 335566 | 20.13% |  | 20 | 266951 | 251675 | 6.07%
21 | 308090 | 223711 | 37.72% |  | 21 | 315824 | 255170 | 23.77% |  | 21 | 405174 | 335566 | 20.74% |  | 21 | 268209 | 251675 | 6.57%
22 | 309777 | 223711 | 38.47% |  | 22 | 318038 | 255170 | 24.64% |  | 22 | 408523 | 335566 | 21.74% |  | 22 | 269925 | 251675 | 7.251%
23 | 305268 | 223711 | 36.46% |  | 23 | 311782 | 255170 | 22.19% |  | 23 | 399911 | 335566 | 19.18% |  | 23 | 265912 | 251675 | 5.657%
24 | 317533 | 223711 | 41.94% |  | 24 | 325440 | 255170 | 27.54% |  | 24 | 417598 | 335566 | 24.45% |  | 24 | 276722 | 251675 | 9.952%
25 | 293076 | 223711 | 31.01% |  | 25 | 300184 | 255170 | 17.64% |  | 25 | 385436 | 335566 | 14.86% |  | 25 | 255486 | 251675 | 1.514%
26 | 259804 | 223711 | 16.13% |  | 26 | 266026 | 255170 | 4.254% |  | 26 | 341420 | 335566 | 1.745% |  | 26 | 227449 | 251675 | -9.626%
27 | 328446 | 223711 | 46.82% |  | 27 | 336337 | 255170 | 31.81% |  | 27 | 431958 | 335566 | 28.73% |  | 27 | 285563 | 251675 | 13.46%
28 | 318694 | 223711 | 42.46% |  | 28 | 326140 | 255170 | 27.81% |  | 28 | 420838 | 335566 | 25.41% |  | 28 | 277045 | 251675 | 10.08%
29 | 318034 | 223711 | 42.16% |  | 29 | 326804 | 255170 | 28.07% |  | 29 | 418694 | 335566 | 24.77% |  | 29 | 276284 | 251675 | 9.778%
30 | 288669 | 223711 | 29.04% |  | 30 | 297058 | 255170 | 16.42% |  | 30 | 382756 | 335566 | 14.06% |  | 30 | 252118 | 251675 | 0.176%
31 | 326229 | 223711 | 45.83% |  | 31 | 332993 | 255170 | 30.5% |  | 31 | 430225 | 335566 | 28.21% |  | 31 | 283164 | 251675 | 12.51%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
July | Yield | Target | Variance |  | July | Yield | Target | Variance |  | July | Yield | Target | Variance |  | July | Yield | Target | Variance
1 | 634496 | 621419 | 2.104% |  | 1 | 184580 | 155355 | 18.81% |  | 1 | 912805 | 684103 | 33.43% |  | 1 | 937536 | 781832 | 19.92%
2 | 641370 | 621419 | 3.211% |  | 2 | 185510 | 155355 | 19.41% |  | 2 | 913611 | 684103 | 33.55% |  | 2 | 938878 | 781832 | 20.09%
3 | 610898 | 621419 | -1.693% |  | 3 | 175486 | 155355 | 12.96% |  | 3 | 839840 | 684103 | 22.77% |  | 3 | 871619 | 781832 | 11.48%
4 | 602942 | 621419 | -2.973% |  | 4 | 172609 | 155355 | 11.11% |  | 4 | 768296 | 684103 | 12.31% |  | 4 | 830464 | 781832 | 6.22%
5 | 644350 | 621419 | 3.69% |  | 5 | 184006 | 155355 | 18.44% |  | 5 | 898627 | 684103 | 31.36% |  | 5 | 926793 | 781832 | 18.54%
6 | 650208 | 621419 | 4.633% |  | 6 | 187872 | 155355 | 20.93% |  | 6 | 919791 | 684103 | 34.45% |  | 6 | 948520 | 781832 | 21.32%
7 | 537808 | 621419 | -13.45% |  | 7 | 156516 | 155355 | 0.7473% |  | 7 | 727082 | 684103 | 6.283% |  | 7 | 754776 | 781832 | -3.461%
8 | 620550 | 621419 | -0.1398% |  | 8 | 176454 | 155355 | 13.58% |  | 8 | 846252 | 684103 | 23.7% |  | 8 | 876082 | 781832 | 12.06%
9 | 232497 | 621419 | -62.59% |  | 9 | 67688 | 155355 | -56.43% |  | 9 | 289330 | 684103 | -57.71% |  | 9 | 322850 | 781832 | -58.71%
10 | 502606 | 621419 | -19.12% |  | 10 | 141594 | 155355 | -8.858% |  | 10 | 631195 | 684103 | -7.734% |  | 10 | 685357 | 781832 | -12.34%
11 | 251461 | 621419 | -59.53% |  | 11 | 72073 | 155355 | -53.61% |  | 11 | 302174 | 684103 | -55.83% |  | 11 | 352115 | 781832 | -54.96%
12 | 687939 | 621419 | 10.7% |  | 12 | 188524 | 155355 | 21.35% |  | 12 | 926257 | 684103 | 35.4% |  | 12 | 992507 | 781832 | 26.95%
13 | 447677 | 621419 | -27.96% |  | 13 | 125179 | 155355 | -19.42% |  | 13 | 581896 | 684103 | -14.94% |  | 13 | 621778 | 781832 | -20.47%
14 | 60528 | 621419 | -90.26% |  | 14 | 16719 | 155355 | -89.24% |  | 14 | 63312 | 684103 | -90.75% |  | 14 | 73679 | 781832 | -90.58%
15 | 683884 | 621419 | 10.05% |  | 15 | 194833 | 155355 | 25.41% |  | 15 | 946569 | 684103 | 38.37% |  | 15 | 1005503 | 781832 | 28.61%
16 | 471470 | 621419 | -24.13% |  | 16 | 128658 | 155355 | -17.18% |  | 16 | 664107 | 684103 | -2.923% |  | 16 | 693370 | 781832 | -11.31%
17 | 676914 | 621419 | 8.93% |  | 17 | 196999 | 155355 | 26.81% |  | 17 | 954468 | 684103 | 39.52% |  | 17 | 1019311 | 781832 | 30.37%
18 | 671712 | 621419 | 8.093% |  | 18 | 189821 | 155355 | 22.19% |  | 18 | 922778 | 684103 | 34.89% |  | 18 | 987260 | 781832 | 26.28%
19 | 636697 | 621419 | 2.459% |  | 19 | 186874 | 155355 | 20.29% |  | 19 | 894763 | 684103 | 30.79% |  | 19 | 956782 | 781832 | 22.38%
20 | 658407 | 621419 | 5.952% |  | 20 | 193514 | 155355 | 24.56% |  | 20 | 918840 | 684103 | 34.31% |  | 20 | 982591 | 781832 | 25.68%
21 | 664836 | 621419 | 6.987% |  | 21 | 196002 | 155355 | 26.16% |  | 21 | 930644 | 684103 | 36.04% |  | 21 | 999282 | 781832 | 27.81%
22 | 666988 | 621419 | 7.333% |  | 22 | 196689 | 155355 | 26.61% |  | 22 | 931828 | 684103 | 36.21% |  | 22 | 998796 | 781832 | 27.75%
23 | 658940 | 621419 | 6.038% |  | 23 | 193184 | 155355 | 24.35% |  | 23 | 913297 | 684103 | 33.5% |  | 23 | 972192 | 781832 | 24.35%
24 | 681692 | 621419 | 9.699% |  | 24 | 202049 | 155355 | 30.06% |  | 24 | 964727 | 684103 | 41.02% |  | 24 | 1030828 | 781832 | 31.85%
25 | 625397 | 621419 | 0.6401% |  | 25 | 172607 | 155355 | 11.1% |  | 25 | 819570 | 684103 | 19.8% |  | 25 | 865904 | 781832 | 10.75%
26 | 554054 | 621419 | -10.84% |  | 26 | 165022 | 155355 | 6.223% |  | 26 | 726729 | 684103 | 6.231% |  | 26 | 775298 | 781832 | -0.8357%
27 | 703543 | 621419 | 13.22% |  | 27 | 202287 | 155355 | 30.21% |  | 27 | 959054 | 684103 | 40.19% |  | 27 | 1021662 | 781832 | 30.68%
28 | 686243 | 621419 | 10.43% |  | 28 | 189997 | 155355 | 22.3% |  | 28 | 904303 | 684103 | 32.19% |  | 28 | 967376 | 781832 | 23.73%
29 | 685439 | 621419 | 10.3% |  | 29 | 205596 | 155355 | 32.34% |  | 29 | 985223 | 684103 | 44.02% |  | 29 | 1050521 | 781832 | 34.37%
30 | 640274 | 621419 | 3.034% |  | 30 | 185510 | 155355 | 19.41% |  | 30 | 870662 | 684103 | 27.27% |  | 30 | 933457 | 781832 | 19.39%
31 | 733671 | 621419 | 18.06% |  | 31 | 207564 | 155355 | 33.61% |  | 31 | 981671 | 684103 | 43.5% |  | 31 | 1049261 | 781832 | 34.21%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 8373.501
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 8370.931
| 2020-07-01 | 1 |  | 1094.6 |  | 2020-07-01 | 1 |  | 274 |  | 2020-07-01 | 1 |  | 273.3 |  | Pl72C | 11031.308
| 2020-07-02 | 1 |  | 1089.6 |  | 2020-07-02 | 1 |  | 272.6 |  | 2020-07-02 | 1 |  | 272.2 |  | PL-R3 | 17590.995
| 2020-07-03 | 1 |  | 1031.4 |  | 2020-07-03 | 1 |  | 258.4 |  | 2020-07-03 | 1 |  | 257.3 |  | STP60 | 31500.6
| 2020-07-06 | 3 |  | 3234.8 |  | 2020-07-06 | 3 |  | 808.8 |  | 2020-07-06 | 3 |  | 808.6 |  | STP20-F | 5057.436
| 2020-07-07 | 1 |  | 932 |  | 2020-07-07 | 1 |  | 233 |  | 2020-07-07 | 1 |  | 233 |  | West wing | 7309.478
| 2020-07-10 | 3 |  | 2215.4 |  | 2020-07-10 | 3 |  | 544.8 |  | 2020-07-10 | 3 |  | 562.9 |  | Tracker-1 | 23996.896
| 2020-07-13 | 3 |  | 2510.4 |  | 2020-07-13 | 3 |  | 631.5 |  | 2020-07-13 | 3 |  | 623.7 |  | Tracker-2 | 25504.812
| 2020-07-14 | 1 |  | 106.2 |  | 2020-07-14 | 1 |  | 26.4 |  | 2020-07-14 | 1 |  | 26.7
| 2020-07-15 | 1 |  | 1118 |  | 2020-07-15 | 1 |  | 279.4 |  | 2020-07-15 | 1 |  | 279.6 |  |  | kWh | Value
| 2020-07-16 | 1 |  | 817.2 |  | 2020-07-16 | 1 |  | 204.5 |  | 2020-07-16 | 1 |  | 204.1 |  | Plant total | 138735.957 | 249724.7226
| 2020-07-17 | 1 |  | 1156.8 |  | 2020-07-17 | 1 |  | 289.1 |  | 2020-07-17 | 1 |  | 289.3 |  | Janitza | 120400 | 216720
| 2020-07-20 | 3 |  | 3485 |  | 2020-07-20 | 3 |  | 870.9 |  | 2020-07-20 | 3 |  | 871.6 |  | Difference | 18335.957 | 33004.7226
| 2020-07-21 | 1 |  | 0 |  | 2020-07-21 | 1 |  |  |  | 2020-07-21 | 1 |  |  |  |  | 86.78% | 86.78%
| 2020-07-22 | 1 |  | 0 |  | 2020-07-22 | 1 |  |  |  | 2020-07-22 | 1
| 2020-07-23 | 1 |  | 3457.6 |  | 2020-07-23 | 1 |  | 864.1 |  | 2020-07-23 | 1 |  | 864.7
| 2020-07-24 | 1 |  | 1183.6 |  | 2020-07-24 | 1 |  | 294.9 |  | 2020-07-24 | 1 |  | 296.9
| 2020-07-27 | 3 |  | 3306.4 |  | 2020-07-27 | 3 |  | 826.1 |  | 2020-07-27 | 3 |  | 827.1
| 2020-07-28 | 1 |  | 1211 |  | 2020-07-28 | 1 |  | 302.4 |  | 2020-07-28 | 1 |  | 303.1
| 2020-07-29 | 1 |  | 1203.2 |  | 2020-07-29 | 1 |  | 300.6 |  | 2020-07-29 | 1 |  | 301
| 2020-07-30 | 1 |  | 1124.2 |  | 2020-07-30 | 1 |  | 280.5 |  | 2020-07-30 | 1 |  | 281.6
| 2020-07-31 | 1 |  | 1223.2 |  | 2020-07-31 | 1 |  | 305.4 |  | 2020-07-31 | 1 |  | 306.2
|  | 31 |  | 31500.6

## Aug 20
East wing | Inverter: | Platinum 7200TLD |  |  | Centre | Inverter: | Platinum 22000TLD |  |  | Centre | Inverter: | Platinum 7200TLD |  |  | West wing | Inverter: | Platinum 7200TLD
Azimuth | 10° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | -10° | Tilt | 30°
August | Yield | Target | Variance |  | August | Yield | Target | Variance |  | August | Yield | Target | Variance |  | August | Yield | Target | Variance
1 | 316837 | 255670 | 23.92% |  | 1 | 326163 | 291623 | 11.84% |  | 1 | 419319 | 383505 | 9.339% |  | 1 | 275635 | 287628 | -4.17%
2 | 324193 | 255670 | 26.8% |  | 2 | 330885 | 291623 | 13.46% |  | 2 | 426702 | 383505 | 11.26% |  | 2 | 282536 | 287628 | -1.77%
3 | 324987 | 255670 | 27.11% |  | 3 | 330711 | 291623 | 13.4% |  | 3 | 428368 | 383505 | 11.7% |  | 3 | 282118 | 287628 | -1.916%
4 | 211921 | 255670 | -17.11% |  | 4 | 219226 | 291623 | -24.83% |  | 4 | 278635 | 383505 | -27.35% |  | 4 | 185759 | 287628 | -35.42%
5 | 136969 | 255670 | -46.43% |  | 5 | 140810 | 291623 | -51.72% |  | 5 | 180547 | 383505 | -52.92% |  | 5 | 120812 | 287628 | -58%
6 | 263459 | 255670 | 3.047% |  | 6 | 264147 | 291623 | -9.422% |  | 6 | 340671 | 383505 | -11.17% |  | 6 | 228612 | 287628 | -20.52%
7 | 287082 | 255670 | 12.29% |  | 7 | 290960 | 291623 | -0.2273% |  | 7 | 379650 | 383505 | -1.005% |  | 7 | 248735 | 287628 | -13.52%
8 | 298013 | 255670 | 16.56% |  | 8 | 301429 | 291623 | 3.363% |  | 8 | 390941 | 383505 | 1.939% |  | 8 | 258212 | 287628 | -10.23%
9 | 333806 | 255670 | 30.56% |  | 9 | 338277 | 291623 | 16% |  | 9 | 439849 | 383505 | 14.69% |  | 9 | 290831 | 287628 | 1.114%
10 | 329218 | 255670 | 28.77% |  | 10 | 334715 | 291623 | 14.78% |  | 10 | 431328 | 383505 | 12.47% |  | 10 | 286191 | 287628 | -0.4996%
11 | 348739 | 255670 | 36.4% |  | 11 | 352598 | 291623 | 20.91% |  | 11 | 458483 | 383505 | 19.55% |  | 11 | 303417 | 287628 | 5.489%
12 | 358308 | 255670 | 40.14% |  | 12 | 361374 | 291623 | 23.92% |  | 12 | 470914 | 383505 | 22.79% |  | 12 | 311167 | 287628 | 8.184%
13 | 143824 | 255670 | -43.75% |  | 13 | 148488 | 291623 | -49.08% |  | 13 | 188581 | 383505 | -50.83% |  | 13 | 125196 | 287628 | -56.47%
14 | 353027 | 255670 | 38.08% |  | 14 | 356062 | 291623 | 22.1% |  | 14 | 463591 | 383505 | 20.88% |  | 14 | 307214 | 287628 | 6.809%
15 | 248756 | 255670 | -2.704% |  | 15 | 250571 | 291623 | -14.08% |  | 15 | 324529 | 383505 | -15.38% |  | 15 | 217738 | 287628 | -24.3%
16 | 247525 | 255670 | -3.186% |  | 16 | 248061 | 291623 | -14.94% |  | 16 | 322566 | 383505 | -15.89% |  | 16 | 216272 | 287628 | -24.81%
17 | 149778 | 255670 | -41.42% |  | 17 | 152760 | 291623 | -47.62% |  | 17 | 196661 | 383505 | -48.72% |  | 17 | 131252 | 287628 | -54.37%
18 | 140117 | 255670 | -45.2% |  | 18 | 143390 | 291623 | -50.83% |  | 18 | 184605 | 383505 | -51.86% |  | 18 | 122784 | 287628 | -57.31%
19 | 196838 | 255670 | -23.01% |  | 19 | 199394 | 291623 | -31.63% |  | 19 | 257448 | 383505 | -32.87% |  | 19 | 173524 | 287628 | -39.67%
20 | 264415 | 255670 | 3.42% |  | 20 | 266154 | 291623 | -8.734% |  | 20 | 344934 | 383505 | -10.06% |  | 20 | 231741 | 287628 | -19.43%
21 | 357342 | 255670 | 39.77% |  | 21 | 360309 | 291623 | 23.55% |  | 21 | 469699 | 383505 | 22.48% |  | 21 | 310437 | 287628 | 7.93%
22 | 371009 | 255670 | 45.11% |  | 22 | 370488 | 291623 | 27.04% |  | 22 | 485706 | 383505 | 26.65% |  | 22 | 322133 | 287628 | 12%
23 | 379640 | 255670 | 48.49% |  | 23 | 381348 | 291623 | 30.77% |  | 23 | 497288 | 383505 | 29.67% |  | 23 | 330064 | 287628 | 14.75%
24 | 131433 | 255670 | -48.59% |  | 24 | 131638 | 291623 | -54.86% |  | 24 | 170888 | 383505 | -55.44% |  | 24 | 114957 | 287628 | -60.03%
25 | 363954 | 255670 | 42.35% |  | 25 | 361176 | 291623 | 23.85% |  | 25 | 473514 | 383505 | 23.47% |  | 25 | 314617 | 287628 | 9.383%
26 | 335028 | 255670 | 31.04% |  | 26 | 338693 | 291623 | 16.14% |  | 26 | 435776 | 383505 | 13.63% |  | 26 | 293504 | 287628 | 2.043%
27 | 364920 | 255670 | 42.73% |  | 27 | 363702 | 291623 | 24.72% |  | 27 | 475673 | 383505 | 24.03% |  | 27 | 317484 | 287628 | 10.38%
28 | 305687 | 255670 | 19.56% |  | 28 | 324997 | 291623 | 11.44% |  | 28 | 424129 | 383505 | 10.59% |  | 28 | 313470 | 287628 | 8.985%
29 | 285125 | 255670 | 11.52% |  | 29 | 329857 | 291623 | 13.11% |  | 29 | 428505 | 383505 | 11.73% |  | 29 | 325993 | 287628 | 13.34%
30 | 247164 | 255670 | -3.327% |  | 30 | 286982 | 291623 | -1.591% |  | 30 | 367935 | 383505 | -4.06% |  | 30 | 279824 | 287628 | -2.713%
31 | 271092 | 255670 | 6.032% |  | 31 | 294824 | 291623 | 1.098% |  | 31 | 418060 | 383505 | 9.01% |  | 31 | 325755 | 287628 | 13.26%
Centre | Inverter: | Platinum R3 16000 |  |  | Centre | Inverter: | SMA 20k Fixed |  |  | Centre | Inverter: | Tracker section 1 |  |  | Centre | Inverter: | Tracker section 2
Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | n/a | Tilt | n/a |  | Azimuth | n/a | Tilt | n/a
August | Yield | Target | Variance |  | August | Yield | Target | Variance |  | August | Yield | Target | Variance |  | August | Yield | Target | Variance
1 | 711440 | 710194 | 0.1754% |  | 1 | 204392 | 177548 | 15.12% |  | 1 | 971406 | 781832 | 24.25% |  | 1 | 1039440 | 893523 | 16.33%
2 | 731851 | 710194 | 3.049% |  | 2 | 199586 | 177548 | 12.41% |  | 2 | 931861 | 781832 | 19.19% |  | 2 | 996404 | 893523 | 11.51%
3 | 733513 | 710194 | 3.283% |  | 3 | 201574 | 177548 | 13.53% |  | 3 | 950250 | 781832 | 21.54% |  | 3 | 1012615 | 893523 | 13.33%
4 | 472959 | 710194 | -33.4% |  | 4 | 138722 | 177548 | -21.87% |  | 4 | 598337 | 781832 | -23.47% |  | 4 | 671372 | 893523 | -24.86%
5 | 310889 | 710194 | -56.22% |  | 5 | 86603 | 177548 | -51.22% |  | 5 | 349261 | 781832 | -55.33% |  | 5 | 397726 | 893523 | -55.49%
6 | 593639 | 710194 | -16.41% |  | 6 | 169502 | 177548 | -4.532% |  | 6 | 738667 | 781832 | -5.521% |  | 6 | 808220 | 893523 | -9.547%
7 | 649702 | 710194 | -8.518% |  | 7 | 176024 | 177548 | -0.8584% |  | 7 | 819738 | 781832 | 4.848% |  | 7 | 882582 | 893523 | -1.224%
8 | 666636 | 710194 | -6.133% |  | 8 | 181560 | 177548 | 2.26% |  | 8 | 843593 | 781832 | 7.9% |  | 8 | 911572 | 893523 | 2.02%
9 | 753578 | 710194 | 6.109% |  | 9 | 212207 | 177548 | 19.52% |  | 9 | 961372 | 781832 | 22.96% |  | 9 | 1039005 | 893523 | 16.28%
10 | 739626 | 710194 | 4.144% |  | 10 | 212067 | 177548 | 19.44% |  | 10 | 994927 | 781832 | 27.26% |  | 10 | 1067528 | 893523 | 19.47%
11 | 790193 | 710194 | 11.26% |  | 11 | 223266 | 177548 | 25.75% |  | 11 | 1037239 | 781832 | 32.67% |  | 11 | 1112988 | 893523 | 24.56%
12 | 812317 | 710194 | 14.38% |  | 12 | 227683 | 177548 | 28.24% |  | 12 | 1065765 | 781832 | 36.32% |  | 12 | 1140772 | 893523 | 27.67%
13 | 321186 | 710194 | -54.77% |  | 13 | 92256 | 177548 | -48.04% |  | 13 | 392936 | 781832 | -49.74% |  | 13 | 418516 | 893523 | -53.16%
14 | 799323 | 710194 | 12.55% |  | 14 | 213854 | 177548 | 20.45% |  | 14 | 993757 | 781832 | 27.11% |  | 14 | 1033389 | 893523 | 15.65%
15 | 562489 | 710194 | -20.8% |  | 15 | 158179 | 177548 | -10.91% |  | 15 | 636911 | 781832 | -18.54% |  | 15 | 695602 | 893523 | -22.15%
16 | 555384 | 710194 | -21.8% |  | 16 | 154582 | 177548 | -12.94% |  | 16 | 654918 | 781832 | -16.23% |  | 16 | 689466 | 893523 | -22.84%
17 | 338628 | 710194 | -52.32% |  | 17 | 95158 | 177548 | -46.4% |  | 17 | 408603 | 781832 | -47.74% |  | 17 | 434717 | 893523 | -51.35%
18 | 316883 | 710194 | -55.38% |  | 18 | 89701 | 177548 | -49.48% |  | 18 | 362734 | 781832 | -53.6% |  | 18 | 389820 | 893523 | -56.37%
19 | 441948 | 710194 | -37.77% |  | 19 | 125912 | 177548 | -29.08% |  | 19 | 510661 | 781832 | -34.68% |  | 19 | 544497 | 893523 | -39.06%
20 | 597987 | 710194 | -15.8% |  | 20 | 164024 | 177548 | -7.617% |  | 20 | 715983 | 781832 | -8.422% |  | 20 | 750365 | 893523 | -16.02%
21 | 811254 | 710194 | 14.23% |  | 21 | 226774 | 177548 | 27.73% |  | 21 | 1047047 | 781832 | 33.92% |  | 21 | 1062925 | 893523 | 18.96%
22 | 841246 | 710194 | 18.45% |  | 22 | 235158 | 177548 | 32.45% |  | 22 | 1071777 | 781832 | 37.09% |  | 22 | 1076923 | 893523 | 20.53%
23 | 858627 | 710194 | 20.9% |  | 23 | 243342 | 177548 | 37.06% |  | 23 | 1098066 | 781832 | 40.45% |  | 23 | 1122328 | 893523 | 25.61%
24 | 295722 | 710194 | -58.36% |  | 24 | 81430 | 177548 | -54.14% |  | 24 | 291751 | 781832 | -62.68% |  | 24 | 351178 | 893523 | -60.7%
25 | 822477 | 710194 | 15.81% |  | 25 | 229575 | 177548 | 29.3% |  | 25 | 1014166 | 781832 | 29.72% |  | 25 | 1064136 | 893523 | 19.09%
26 | 738939 | 710194 | 4.047% |  | 26 | 216051 | 177548 | 21.69% |  | 26 | 959316 | 781832 | 22.7% |  | 26 | 977834 | 893523 | 9.436%
27 | 821299 | 710194 | 15.64% |  | 27 | 231738 | 177548 | 30.52% |  | 27 | 1055442 | 781832 | 35% |  | 27 | 1072971 | 893523 | 20.08%
28 | 777073 | 710194 | 9.417% |  | 28 | 209156 | 177548 | 17.8% |  | 28 | 939650 | 781832 | 20.19% |  | 28 | 1018690 | 893523 | 14.01%
29 | 786894 | 710194 | 10.8% |  | 29 | 212560 | 177548 | 19.72% |  | 29 | 927909 | 781832 | 18.68% |  | 29 | 1013200 | 893523 | 13.39%
30 | 674779 | 710194 | -4.987% |  | 30 | 175531 | 177548 | -1.136% |  | 30 | 708766 | 781832 | -9.345% |  | 30 | 786141 | 893523 | -12.02%
31 | 770983 | 710194 | 8.559% |  | 31 | 204343 | 177548 | 15.09% |  | 31 | 817081 | 781832 | 4.509% |  | 31 | 871792 | 893523 | -2.432%
| Centre | Inverter: | SMA 60k-All Fixed |  |  | Centre | Inverter: | SMA 60k-1 Fixed |  |  | Centre | Inverter: | SMA 60k-2 Fixed |  |  | NMU Plant | Inverters
| Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | Azimuth | 0° | Tilt | 30° |  | East wing | 8690.206
| Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | Date | Days | Reading | kWh |  | PL22k | 8900.189
| 2020-08-03 | 3 |  | 3640 |  | 2020-07-31 |  | 112015.9 | 305.4 |  | 2020-07-31 |  | 107850.8 | 306.2 |  | Pl72C | 11575.495
| 2020-08-04 | 1 |  | 847.8 |  | 2020-08-03 | 3 | 112924.6 | 908.7 |  | 2020-08-03 | 3 | 108762.1 | 911.3 |  | PL-R3 | 20099.464
| 2020-08-05 | 1 |  | 575.4 |  | 2020-08-04 | 1 | 113140.5 | 215.9 |  | 2020-08-04 | 1 | 108970.1 | 208 |  | STP60 | 33800.2
| 2020-08-06 | 1 |  | 949.4 |  | 2020-08-05 | 1 | 113280.1 | 139.6 |  | 2020-08-05 | 1 | 109118.2 | 148.1 |  | STP20-F | 5592.51
| 2020-08-07 | 1 |  | 1062.6 |  | 2020-08-06 | 1 | 113517.3 | 237.2 |  | 2020-08-06 | 1 | 109355.7 | 237.5 |  | West wing | 7847.984
| 2020-08-11 | 4 |  | 4969.8 |  | 2020-08-07 | 1 | 113782.6 | 265.3 |  | 2020-08-07 | 1 | 109621.7 | 266 |  | Tracker-1 | 24869.89
| 2020-08-12 | 1 |  | 1345.2 |  | 2020-08-11 | 4 | 115023.1 | 1240.5 |  | 2020-08-11 | 4 | 110866.1 | 1244.4 |  | Tracker-2 | 26454.714
| 2020-08-13 | 1 |  | 596.8 |  | 2020-08-12 | 1 | 115358.7 | 335.6 |  | 2020-08-12 | 1 | 111203.1 | 337
| 2020-08-14 | 1 |  | 1287.2 |  | 2020-08-13 | 1 | 115507.3 | 148.6 |  | 2020-08-13 | 1 | 111352.9 | 149.8 |  | Plant total | 147830.652
| 2020-08-17 | 3 |  | 2522.2 |  | 2020-08-14 | 1 | 115828.9 | 321.6 |  | 2020-08-14 | 1 | 111674.9 | 322 |  | Janitza | 114252.5
| 2020-08-18 | 1 |  | 541.8 |  | 2020-08-17 | 3 | 116457.3 | 628.4 |  | 2020-08-17 | 3 | 112307.6 | 632.7 |  | Difference | 33578.152
| 2020-08-19 | 1 |  | 763 |  | 2020-08-18 | 1 | 116593.1 | 135.8 |  | 2020-08-18 | 1 | 112442.7 | 135.1 |  |  | 77.29%
| 2020-08-20 | 1 |  | 984.4 |  | 2020-08-19 | 1 | 116783.5 | 190.4 |  | 2020-08-19 | 1 | 112633.8 | 191.1
| 2020-08-21 | 1 |  | 1267 |  | 2020-08-20 | 1 | 117029 | 245.5 |  | 2020-08-20 | 1 | 112880.5 | 246.7
| 2020-08-24 | 3 |  | 3637 |  | 2020-08-21 | 1 | 117345.9 | 316.9 |  | 2020-08-21 | 1 | 113197.1 | 316.6
| 2020-08-25 | 1 |  | 1057.6 |  | 2020-08-24 | 3 | 118253 | 907.1 |  | 2020-08-24 | 3 | 114108.5 | 911.4
| 2020-08-26 | 1 |  | 1328.6 |  | 2020-08-25 | 1 | 118517 | 264 |  | 2020-08-25 | 1 | 114373.3 | 264.8
| 2020-08-31 | 5 |  | 6424.4 |  | 2020-08-26 | 1 | 118848 | 331 |  | 2020-08-26 | 1 | 114706.6 | 333.3
[6 empty] | 2020-08-31 | 5 | 120450.7 | 1602.7 |  | 2020-08-31 | 5 | 116316.1 | 1609.5
|  | 31 |  | 33800.2
[7 empty] | 31 | 8434.8 | 8434.8 |  |  | 31 | 8465.3 | 8465.3